## FR_OCR (hidden)
Timestamp | Role User Input | ULTG | GI / GIS | GI / GIS 2 | GI / GIS 3 | BAY | PHT & KOPEL | BAY 2 | PHT & KOPEL 2 | BAY 3 | PHT & KOPEL 3 | BAY 4 | PHT & KOPEL 4 | BAY 5 | PHT & KOPEL 5 | BAY 6 | PHT & KOPEL 6 | BAY 7 | PHT & KOPEL 7 | BAY 8 | PHT & KOPEL 8 | BAY 9 | PHT & KOPEL 9 | BAY 10 | PHT & KOPEL 10 | BAY 11 | PHT & KOPEL 11 | BAY 12 | PHT & KOPEL 12 | BAY 13 | PHT & KOPEL 13 | BAY 14 | BAY PHT & KOPEL | BAY 15 | PHT & KOPEL 14 | BAY 16 | PHT & KOPEL 15 | BAY 17 | PHT & KOPEL 16 | BAY 18 | PHT & KOPEL 17 | BAY 19 | PHT & KOPEL 18 | BAY 20 | PHT & KOPEL 19 | BAY 21 | PHT & KOPEL 20 | BAY 22 | PHT & KOPEL 21 | BAY 23 | PHT & KOPEL 22 | BAY 24 | PHT & KOPEL 23 | BAY 25 | PHT & KOPEL 24 | BAY 26 | PHT & KOPEL 25 | BAY 27 | PHT & KOPEL 26 | BAY 28 | PHT & KOPEL 27 | BAY 29 | PHT & KOPEL 28 | BAY 30 | PHT & KOPEL 29 | BAY 31 | PHT & KOPEL 30 | BAY 32 | PHT & KOPEL 31 | BAY 33 | PHT & KOPEL 32 | BAY 34 | PHT & KOPEL 33 | BAY 35 | PHT & KOPEL 34 | CT Ratio - Primary | CT Ratio - Secondary | Merk Relay | Tipe Relay | Nomor Seri Relay | Iset OC | tms OC | karakteristik OC | Iset OC Instant | tms OC Instant | karakteristik OC Instant | Iset GF | tms GF | karakteristik GF | Iset GF Instant | tms GF Instant | karakteristik GF Instant | TRAFO/IBT | CT Ratio HV - Primary | CT Ratio HV - Secondary | CT Ratio LV - Primary | CT Ratio LV - Secondary | CT Ratio SBEF - Primary | CT Ratio SBEF - Secondary | Merk / Tipe Relay - OCR/GFR HV | I > | t I > | Char I > | I >> | t I >> | Char I >> | Ie > | t Ie > | Char Ie > | Ie >> | t Ie >> | Char Ie >> | Merk / Tipe Relay - OCR/GFR LV | I > 2 | t I > 2 | Char I > 2 | I >> 2 | t I >> 2 | Char I >> 2 | Ie > 2 | t Ie > 2 | Char Ie > 2 | Ie >> 2 | t Ie >> 2 | Char Ie >> 2 | Merk / Tipe Relay - SBEF | I > 3 | t I > 3 | Char I > 3 | I >> 3 | t I >> 3 | Char I >> 3 | Ie > 3 | t Ie > 3 | Char Ie > 3 | Ie >> 3 | t Ie >> 3 | Char Ie >> 3 | Tanggal Rilis Tap Setting Terakhir | Upload File Tap Setting Terakhir | Jenis Relay | Tahun Operasi
2025-12-22 16:35 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 | GE Alstom | Micom P841 |  | 1.2 | 432 | SI |  |  |  | 0 | 0 | SI
2025-12-22 16:38 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 | GE Alstom | Micom P841 |  | 1.2 | 432 | SI |  |  |  | 0 | 0 | SI
2025-12-22 16:41 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 | GE Alstom | Micom P841 |  | 1.2 | 432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 16:52 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 |  |  |  | 1.2 | 432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 17:03 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 | GE | P841 |  | 1.2 | 432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 17:03 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 |  |  |  | 1.2 | 432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 17:05 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 5 | GE Alstom | Micom P841 | 1234567 | 1.2 | 432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 17:07 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 |  |  |  | 1.3 | 444 | SI |  |  |  | 0 | 0 | DT
2025-12-22 17:23 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 |  |  |  | 1.2 | 0.432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 17:27 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 |  |  |  | 1.2 | 0.432 | SI |  |  |  | 0 | 0 | Lainnya
2025-12-22 17:37 | ASDIG | ULTG ANGKE | GI 150KV DADAP |  |  |  |  | PHT & KOPEL | KOPEL 150kV | [66 empty] | 4000 | 1 |  |  |  | 1.2 | 0.432 | SI |  |  |  | 0 | 0 | blok | [51 empty] | Numerik

## Rekap
DATA RELE
|  | Main Prot | 0
|  | Backup | 0
|  |  | Numerik | Elektromekanik | Obsolet
|  | Main Prot | 0 | 0 | 0
| 0 | Backup | 0 | 0 | 0
HEALTH INDEX
|  |  | 0 | 0 | 0
|  |  | 9 | 6 | 1
|  | Main Prot | 0 | 0 | 0
|  | Backup | 0 | 0 | 0
HEALTH INDEX - MAIN PROT
|  |  | Buspro | LCD | DIFF 500 (MAIN B)
|  | Tidak Ada | 1 | #REF! | 0
|  | Tidak Aktif | 1 | #REF! | 0
|  | Belum Aktif | 1 | #REF! | 0
Elektromekanik
|  | DIFF 150 | 0
HEALTH INDEX - BACKUP PROT
|  |  | Elektromekanik | Obsolet
|  | OCR PHT | 0 | 0
|  | OCR HV | 0 | 0
|  | OCR LV | 0 | 0
|  | SBEF | 0 | 0

## MASTER_PHT
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | RATIO CT - MPU | RATIO CT - BPU | RATIO PT | HELPER | HELPER ASET SEKUNDER | [9 empty] | HELPER TOOLS KALKULASI
[9 empty] | GI/GIS | BAY | SIRKIT | CT |  | PT |  | RELAY MPU |  |  | PANJANG PHT | CCC | TIPE KONDUKTOR | mm konduktor | PANJANG PHT | CCC | TIPE KONDUKTOR | mm konduktor | SEGMEN 1 |  | SEGMEN 2 |  | HELPER SHEET SCANNING KOORDINASI PHT | HELPER SHEET IMPLEMENTASI SETTING | JENIS PHT
[12 empty] | PRI | SEC | PRI | SEC | JENIS | SKEMA AR | SYNCHRO | https://docs.google.com/spreadsheets/d/1mp1-eOq9kSt8qW4khlQvSFfgBSTCmTRHZWDiV-XB7a0/edit?gid=1921826523#gid=1921826523 |  |  |  | *MANUAL EDIT SESUAI 4 KOLOM SEBELUMNYA |  |  |  | REAL | ALIAS | REAL | ALIAS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34
PHT.01 | 1 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV ANCOL #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 4.6 | 1766 | ACCC Warsaw | 574.9 | ANGKE | ANGKE | ANCOL | ANCOL | https://docs.google.com/spreadsheets/d/1y2ldFxBgPbX7fXSg1DEK_zHI8X8eMCvE9OeZNVn67ns/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1_feMC27xQFEnCmytl4JDOBOWFZPWBcca_pqeWjEp_Wc/edit?usp=drive_link | SUTT
PHT.02 | 2 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV ANCOL #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 4.6 | 1766 | ACCC Warsaw | 574.9 | ANGKE | ANGKE | ANCOL | ANCOL | https://docs.google.com/spreadsheets/d/1y2ldFxBgPbX7fXSg1DEK_zHI8X8eMCvE9OeZNVn67ns/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1ZKPej-AGG0QtAnPVT1f1-UdGKVZ6JPwo-SlTcIef0Cw/edit?usp=drive_link | SUTT
PHT.03 | 3 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#1 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV KARET LAMA #1 | #1 | 4000 | 5 | 150 | 100 V | DIST | Internal |  | No Data | No Data | No Data | No Data | 7.9 | 2650 | HTLS ACFR 315/40 | 2x348,47 | ANGKE | ANGKE | KARET LAMA | KARET | https://docs.google.com/spreadsheets/d/1wSjlqr8Qp16Kjp9je_uRCShFxIXJjkVHN2O9FVV8CfI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1qTIqpv3M4b7ZRFh1Fll3GEGWXwiKFHTKElCF1MX9Cx0/edit?gid=544152550#gid=544152550 | SUTT
PHT.04 | 4 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#2 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV KARET LAMA #2 | #2 | 4000 | 5 | 150 | 100 V | DIST | Internal |  | No Data | No Data | No Data | No Data | 7.9 | 2650 | HTLS ACFR 315/41 | 2x348,47 | ANGKE | ANGKE | KARET LAMA | KARET | https://docs.google.com/spreadsheets/d/1wSjlqr8Qp16Kjp9je_uRCShFxIXJjkVHN2O9FVV8CfI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1qj6Lzay1QbYrp03gjdLecJRnw8A2fSOiQGGwjEc1-RE/edit?usp=drive_link | SUTT
PHT.05 | 5 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV KETAPANG #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 5.5 | 920 | XLPE CU | 1X1000 | ANGKE | ANGKE | KETAPANG | KETAPANG | https://docs.google.com/spreadsheets/d/1E9QAV9mSSIvIFXDXsOyJept1j37cnV8ptbAGtqzTKgA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1MGuDnJQjAXaXIgYMsUYepUsSRu-UBFbbFhzmkb2QyWs/edit?usp=drive_link | SKTT
PHT.06 | 6 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV KETAPANG #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 5.5 | 920 | XLPE CU | 1X1000 | ANGKE | ANGKE | KETAPANG | KETAPANG | https://docs.google.com/spreadsheets/d/1E9QAV9mSSIvIFXDXsOyJept1j37cnV8ptbAGtqzTKgA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/185vGIM_krvzVjYEP75fefF7QNys4Z1ciW9-THtsqxIU/edit?usp=drive_link | SKTT
PHT.07 | 7 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#1 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #1 | #1 | 4000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 4.1 | 1200 | TACSR | 1x410 | 4.1 | 1200 | TACSR | 1x410 | ANGKE | ANGKE | MUARAKARANG LAMA | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1aAi_BgkxQHjK1es1OJ2kmFyKUo0rJ943A3Cz2t1ijoE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1HmSu_VUPIme2KvbscEGPdfpsM5rONe6A_eINQFARbH4/edit?usp=drive_link | SUTT
PHT.08 | 8 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#2 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #2 | #2 | 4000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 4.1 | 1200 | TACSR | 1x410 | 4.1 | 1200 | TACSR | 1x410 | ANGKE | ANGKE | MUARAKARANG LAMA | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1aAi_BgkxQHjK1es1OJ2kmFyKUo0rJ943A3Cz2t1ijoE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/117KSkWV1SUcCvwWvQBe-7qtydrWoDf3LTLqZ-cRBxKc/edit?usp=drive_link | SUTT
PHT.09 | 9 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 4.6 | 1752 | CAB 2XSK2Y | 2x1200 | ANGKE | ANGKE | UGC MUARAKARANG LAMA | UGC MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/17lOA981pkPWADUMV07prdgrAhsIA4_p-co-o4zCGgUU/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1x8x8zV4t51Gk41JCc78MVuYC3wnSzjAg3csMLBbGVL8/edit?usp=drive_link | SKTT
PHT.10 | 10 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 4.6 | 1752 | CAB 2XSK2Y | 2x1200 | ANGKE | ANGKE | UGC MUARAKARANG LAMA | UGC MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/17lOA981pkPWADUMV07prdgrAhsIA4_p-co-o4zCGgUU/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1DaMcxhO1EMx3VFiwcgC0WLlbavsPToE4IZhuJotgdj0/edit?usp=drive_link | SKTT
PHT.11 | 11 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GID 150KV DADAP | PHT 150kV LONTAR #1 | #1 | 4000 | 1 | 150 | 100 V | DIST | Internal |  | 26.271 | 2648 | TACSR | 2X410 | 26.271 | 2648 | TACSR | 2X410 | DADAP | DADAP | LONTAR | PLTU LONTAR | https://docs.google.com/spreadsheets/d/16U2WaOfNgjhl_yTOqtPEyvrI3Gau9I8NmDAlgMzu0as/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1zb-AMDz1Y4yx4LJ4kQxYhfEuYM5_UQ_h1MXrHngQqOk/edit?usp=drive_link | SUTT
PHT.12 | 12 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GID 150KV DADAP | PHT 150kV LONTAR #2 | #2 | 4000 | 1 | 150 | 100 V | DIST | Internal |  | 26.271 | 2648 | TACSR | 2X410 | 26.271 | 2648 | TACSR | 2X410 | DADAP | DADAP | LONTAR | PLTU LONTAR | https://docs.google.com/spreadsheets/d/16U2WaOfNgjhl_yTOqtPEyvrI3Gau9I8NmDAlgMzu0as/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1WVN2za7lQTd2VIPIs-tTixzcZxSU8MZTMqM7oTBrCr8/edit?usp=drive_link | SUTT
PHT.13 | 13 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GID 150KV DADAP | PHT 150kV TELUK NAGA #1 | #1 | 4000 | 1 | 150 | 100 V | DIST | Internal |  | 6.132 | 2648 | TACSR | 2X410 | 6.132 | 2648 | TACSR | 2X410 | DADAP | DADAP | TELUK NAGA | TELUK NAGA | https://docs.google.com/spreadsheets/d/1bN6FjeyXNnoRin3xZ80PRD2yKdCDb6HQy5sWfDVPl0o/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1_7zzuc3kqP8gs0-RvMQZqs__EvVgSALJYksmlBl7RXU/edit?usp=drive_link | SUTT
PHT.14 | 14 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GID 150KV DADAP | PHT 150kV TELUK NAGA #2 | #2 | 4000 | 1 | 150 | 100 V | DIST | Internal |  | 6.132 | 2648 | TACSR | 2X410 | 6.132 | 2648 | TACSR | 2X410 | DADAP | DADAP | TELUK NAGA | TELUK NAGA | https://docs.google.com/spreadsheets/d/1bN6FjeyXNnoRin3xZ80PRD2yKdCDb6HQy5sWfDVPl0o/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1UBstAMlW87TlYf7d0kKptpIhB2xdTGBqKn6_ih40fMc/edit?usp=drive_link | SUTT
PHT.15 | 15 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#1 | 2500/5 | 2500/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #1 | #1 | 2500 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.22 | 2218.7 | XLPE CU | 2x2000 | 0.22 | 2218.7 | XLPE CU | 2x2000 | MUARAKARANG BARU | GI MUARAKARANG BARU | GIS MUARAKARANG BARU | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1Q97YkhsaeLw4O0Lmruzg8sAJwHCBA0KKrApbP6wK2gk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1VxGLKtNFrq3w9160PxX92v0ZfUJC78lcZZT4I8wEaSo/edit?usp=sharing | SKTT
PHT.16 | 16 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#2 | 2500/5 | 2500/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #2 | #2 | 2500 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.22 | 2218.7 | XLPE CU | 2x2000 | 0.22 | 2218.7 | XLPE CU | 2x2000 | MUARAKARANG BARU | GI MUARAKARANG BARU | GIS MUARAKARANG BARU | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1Q97YkhsaeLw4O0Lmruzg8sAJwHCBA0KKrApbP6wK2gk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/14NcijQiUUUrJNgxaXrzHMIV1i8qESxkADZbLcfES6KY/edit?usp=sharing | SKTT
PHT.17 | 17 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#1 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #1 | #1 | 4000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 0.7 | 1684 | XLPE CU | 2x2000 | 0.7 | 1684 | XLPE CU | 2x2000 | MUARAKARANG BARU | GI MUARAKARANG BARU | MUARAKARANG LAMA | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1xn_WnVETGK2wPHXm0wuACIAbh988dTQQcO4qNSN_AWA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1CHCZRetMGgeFImQEF7NwZNsFlRUGwfJ-bQn8Or5-20o/edit?usp=drive_link | SKTT
PHT.18 | 18 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#2 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #2 | #2 | 4000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 0.7 | 1684 | XLPE CU | 2x2000 | 0.7 | 1684 | XLPE CU | 2x2000 | MUARAKARANG BARU | GI MUARAKARANG BARU | MUARAKARANG LAMA | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1xn_WnVETGK2wPHXm0wuACIAbh988dTQQcO4qNSN_AWA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/17jLKzetQ5moSvleindl6n0VJnd_pB_bBMhqmPA0ccus/edit?usp=drive_link | SKTT
PHT.19 | 19 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #1 | #1 | 2000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 4.1 | 1200 | TACSR | 1x410 | 4.1 | 1200 | TACSR | 1x410 | MUARAKARANG LAMA | MUARAKARANG LAMA | ANGKE | ANGKE | https://docs.google.com/spreadsheets/d/1Xc7oCNysSgK0KCoAQk0zMpnWp1kiG_utLET_C5YlnVg/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1bU3CdLZuuvrfJQ9RiGxwRfx0ck10eRFG9B1VYpZvYCU/edit?usp=drive_link | SUTT
PHT.20 | 20 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #2 | #2 | 2000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 4.1 | 1200 | TACSR | 1x410 | 4.1 | 1200 | TACSR | 1x410 | MUARAKARANG LAMA | MUARAKARANG LAMA | ANGKE | ANGKE | https://docs.google.com/spreadsheets/d/1Xc7oCNysSgK0KCoAQk0zMpnWp1kiG_utLET_C5YlnVg/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1YPIrB_myuVj18UC9n3sQMVCPOFOWGoNdFJUiSzP21ZU/edit?usp=drive_link | SUTT
PHT.21 | 21 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#1 | 1200/5 | 1200/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #1 | #1 | 1200 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 14 | 735 | OIL CU | 1x800 | MUARAKARANG LAMA | MUARAKARANG LAMA | BUDIKEMULYAN | BUDI KEMULIAAN | https://docs.google.com/spreadsheets/d/1NayK1ecNpIfT8JJl5gfqwlXYjNorbtQ3_zl0ibRESTM/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1yexP-aydoUDEUEuEoWyp19xlAZ0COr0NnYs18Osgp_U/edit?usp=drive_link | SKTT
PHT.22 | 22 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#2 | 1200/5 | 1200/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #2 | #2 | 1200 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 14 | 735 | OIL CU | 1x800 | MUARAKARANG LAMA | MUARAKARANG LAMA | BUDIKEMULYAN | BUDI KEMULIAAN | https://docs.google.com/spreadsheets/d/1NayK1ecNpIfT8JJl5gfqwlXYjNorbtQ3_zl0ibRESTM/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Pb8of-UR7UstAUi76PlEND2272bwV-msDOVxiUp8STY/edit?usp=drive_link | SKTT
PHT.23 | 23 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #1 | #1 | 2000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 0.7 | 1684 | XLPE CU | 2x2000 | 0.7 | 1684 | XLPE CU | 2x2000 | MUARAKARANG LAMA | MUARAKARANG LAMA | MUARAKARANG BARU | GI MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1oaDAF7TdsXGLMOjP8w5AOLpdhlHks9CUhh64BPrW1xg/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1S2rihWhXy3w5Ww6MHGm6lgCA6W9oU9y_iOhuo-TucH0/edit?usp=drive_link | SKTT
PHT.24 | 24 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #2 | #2 | 2000 | 5 | 150 | 100 V | LCD | Tidak Aktif |  | 0.7 | 1684 | XLPE CU | 2x2000 | 0.7 | 1684 | XLPE CU | 2x2000 | MUARAKARANG LAMA | MUARAKARANG LAMA | MUARAKARANG BARU | GI MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1oaDAF7TdsXGLMOjP8w5AOLpdhlHks9CUhh64BPrW1xg/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1fJKaIBpjVeSkgeh6v32tj35e4KKG3b6u9m04JV_aELA/edit?usp=drive_link | SKTT
PHT.25 | 25 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 4.6 | 1752 | CAB 2XSK2Y | 2x1200 | MUARAKARANG LAMA | UGC MUARAKARANG LAMA | UGC ANGKE | UGC ANGKE | https://docs.google.com/spreadsheets/d/1D5Llm7Z3GG4Oh839Kzkrx7LuuGOlOU9b6dJUibIXVJs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1rbyqufWMloGUbWyrpwEyPX_u-cHww-6bFaYKw-T3Rt0/edit?usp=drive_link | SKTT
PHT.26 | 26 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 4.6 | 1752 | CAB 2XSK2Y | 2x1200 | MUARAKARANG LAMA | UGC MUARAKARANG LAMA | UGC ANGKE | UGC ANGKE | https://docs.google.com/spreadsheets/d/1D5Llm7Z3GG4Oh839Kzkrx7LuuGOlOU9b6dJUibIXVJs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1GhA89opUsE6DY2sgNZ1_11q9NqUSkgCehakKWigHir4/edit?usp=drive_link | SKTT
PHT.27 | 27 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #1 | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 2.63 | 2514 | GTACSR | 2X410 | 2.63 | 2514 | GTACSR | 2X410 | DAAN MOGOT | DAAN MOGOT | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1pFLpcZ-GgV9qvT8xBxABYvIy9vLkq8qV5UuPdrdq6KU/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1X6YT1INoslajhA2bTFUi7EPXzoylquoFS_azi6Oih8Q/edit?usp=drive_link | SUTT
PHT.28 | 28 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#2 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #2 | #2 | 3000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 2.63 | 2514 | GTACSR | 2X410 | 2.63 | 2514 | GTACSR | 2X410 | DAAN MOGOT | DAAN MOGOT | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1pFLpcZ-GgV9qvT8xBxABYvIy9vLkq8qV5UuPdrdq6KU/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1G3gsiHGK3LZk-LYVkMn4Lp_b20qWblsNuM-mr210khk/edit?usp=drive_link | SUTT
PHT.29 | 29 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #1 | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.36 | 2514 | GTACSR | 2X410 | 3.36 | 2514 | GTACSR | 2X410 | DAAN MOGOT | DAAN MOGOT | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1l6EKzlWye3eulw2TcIHdZrImrLQkLa-DZBXaobCdyFk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1nF3Yb-cxvss-mTzXAisCXpRT-x9d3h7daUeEVFqLyfs/edit?usp=drive_link | SUTT
PHT.30 | 30 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#2 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #2 | #2 | 3000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.36 | 2514 | GTACSR | 2X410 | 3.36 | 2514 | GTACSR | 2X410 | DAAN MOGOT | DAAN MOGOT | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1l6EKzlWye3eulw2TcIHdZrImrLQkLa-DZBXaobCdyFk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1b8Ar6yu7d-JedzfZhqR2BYpxHEu0SyHQUtRoaXE3dck/edit?usp=drive_link | SUTT
PHT.31 | 31 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#1 | 1600/1 | 1600/1 | 150 kV/100 V |  | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #1 | #1 | 1600 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 1.78 | 1600 | ACSR | 2x485 | 1.78 | 1600 | ACSR | 2x485 | GROGOL | GROGOL | GROGOL BARU | GROGOL BARU | https://docs.google.com/spreadsheets/d/10eovQaptUGLeJOmyBLc8rpfUN3ly2WDxNmIVKu2YLsE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Uj1gPjF81B0mSfMFdXGmpnwtd063LYrSFByThhgI600/edit?usp=drive_link | SUTT
PHT.32 | 32 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#2 | 1600/1 | 1600/1 | 150 kV/100 V |  | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #2 | #2 | 1600 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 1.78 | 1600 | ACSR | 2x485 | 1.78 | 1600 | ACSR | 2x485 | GROGOL | GROGOL | GROGOL BARU | GROGOL BARU | https://docs.google.com/spreadsheets/d/10eovQaptUGLeJOmyBLc8rpfUN3ly2WDxNmIVKu2YLsE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1zEZexc5bkP17UqfqRgeoSB6PBIt_OpVXjYJdxr3rCqc/edit?usp=drive_link | SUTT
PHT.33 | 33 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV GROGOL | PHT 150kV TOMANG #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.11 | 1191 | XLPE CU | 1x2000 | 4.11 | 1191 | XLPE CU | 1x2000 | GROGOL | GROGOL | TOMANG | TOMANG | https://docs.google.com/spreadsheets/d/1r_0wCS-JeeABSTu3Pi_EzQanm75fhsaas9cmN6DpdzU/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/16KyrtoLa4_wA5ncdvK-LACsFt6b4ckA0XP5vGzG2xwg/edit?usp=drive_link | SKTT
PHT.34 | 34 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV GROGOL | PHT 150kV TOMANG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.11 | 1191 | XLPE CU | 1x2000 | 4.11 | 1191 | XLPE CU | 1x2000 | GROGOL | GROGOL | TOMANG | TOMANG | https://docs.google.com/spreadsheets/d/1r_0wCS-JeeABSTu3Pi_EzQanm75fhsaas9cmN6DpdzU/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/15gmDhpZ_XTW0_Zka9m91Wvf9hcZFQWeeC1JR6TXVxzE/edit?usp=drive_link | SKTT
PHT.35 | 35 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 6.14 | 1600 | ACSR | 2x485 | 6.14 | 1600 | ACSR | 2x485 | GROGOL BARU | GROGOL BARU | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1pSit2otTRj1vaNrZtbFetN2SjIJfxI2px4I4DCP-xzA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1TSpR3FNKHwccw-h73vjdljseZHj5xabxDaJdJMCM3zY/edit?usp=drive_link | SUTT
PHT.36 | 36 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 6.14 | 1600 | ACSR | 2x485 | 6.14 | 1600 | ACSR | 2x485 | GROGOL BARU | GROGOL BARU | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1pSit2otTRj1vaNrZtbFetN2SjIJfxI2px4I4DCP-xzA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1gJ5AmkFJ6o12Zf8eFWzPGKFDOTg1B8bLkB721FSdClI/edit?usp=drive_link | SUTT
PHT.37 | 37 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 1.78 | 1600 | ACSR | 2x485 | 1.78 | 1600 | ACSR | 2x485 | GROGOL BARU | GROGOL BARU | GROGOL | GROGOL | https://docs.google.com/spreadsheets/d/1DJglFPaKVG8LtQP18w1T5lZ3DcXeR-PRBvxTeA0Xkh4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1y_KEthuDmKH7Kmw89cyJGkzUkDYIYRAG2VDfff1zLQ8/edit?usp=drive_link | SUTT
PHT.38 | 38 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 1.78 | 1600 | ACSR | 2x485 | 1.78 | 1600 | ACSR | 2x485 | GROGOL BARU | GROGOL BARU | GROGOL | GROGOL | https://docs.google.com/spreadsheets/d/1DJglFPaKVG8LtQP18w1T5lZ3DcXeR-PRBvxTeA0Xkh4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1-wcH0elM2bE4HU8pItllVy-RmVCos8WejvdoBYK3p3s/edit?usp=drive_link | SUTT
PHT.39 | 39 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#1 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #1 | #1 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 10.2 | 920 | CU | 800 | 10.2 | 920 | CU | 800 | KEBON JERUK | KEBON JERUK | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1z5XkYBrnHTqGQ0_WZ_MyyqNaUAbYcDCZP9yB9c7PX_c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1-rDkfQkizAlX0VLdsvC2PMXvj8PPwlCoVvYlYQu2zVQ/edit?usp=drive_link | SKTT
PHT.40 | 40 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#2 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #2 | #2 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 10.2 | 920 | CU | 800 | 10.2 | 920 | CU | 800 | KEBON JERUK | KEBON JERUK | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1z5XkYBrnHTqGQ0_WZ_MyyqNaUAbYcDCZP9yB9c7PX_c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Pbb3-uQViRHekIu8NQJjGnQy3pB8P5rrLUg3yeIKSck/edit?usp=drive_link | SKTT
PHT.41 | 41 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#1 | 500/5 | 500/5 | 150 kV/100 V |  | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #1 | #1 | 500 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 6.34 | 786 | XLPE CU | 1X1000 | KEBON JERUK | KEBON JERUK | KARET BARU | KARET BARU | https://docs.google.com/spreadsheets/d/1LQDIWBo7xgkq3Bxy3G-XGvIshP0FP7cgIbgPzMWIWUA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1iONbCkN9DcoZYBeLDGSiNEIfzUN_qC0vsLU0QL5YHwQ/edit?usp=drive_link | SKTT
PHT.42 | 42 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#2 | 500/5 | 500/5 | 150 kV/100 V |  | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #2 | #2 | 500 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 6.34 | 786 | XLPE CU | 1X1000 | KEBON JERUK | KEBON JERUK | KARET BARU | KARET BARU | https://docs.google.com/spreadsheets/d/1LQDIWBo7xgkq3Bxy3G-XGvIshP0FP7cgIbgPzMWIWUA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/106ZFohplNWZhl71Pv_x1VAytkny9X2DfHjhD1ztdd6I/edit?usp=drive_link | SKTT
PHT.43 | 43 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.22 | 2218.7 | XLPE CU | 2x2000 | 0.22 | 2218.7 | XLPE CU | 2x2000 | MUARAKARANG BARU | GIS MUARAKARANG BARU | MUARAKARANG BARU | GI MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1utRRF8sqmgYDos36r3yOBIPmzilfoRlku4BX6xilNVQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1_7up2oXNP8bDecvQ03tANwi9DONnbLG1Jq8Hq0k01Mk/edit?usp=drive_link | SKTT
PHT.44 | 44 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.22 | 2218.7 | XLPE CU | 2x2000 | 0.22 | 2218.7 | XLPE CU | 2x2000 | MUARAKARANG BARU | GIS MUARAKARANG BARU | MUARAKARANG BARU | GI MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1utRRF8sqmgYDos36r3yOBIPmzilfoRlku4BX6xilNVQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1w8RYbap1AWwu9vGJ7EC6uW-rT5GbJ4Dy_KJDob-KKkU/edit?usp=drive_link | SKTT
PHT.45 | 45 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 5.6 | 2514 | GTACSR | 2X410 | 5.6 | 2514 | GTACSR | 2X410 | MUARAKARANG BARU | GIS MUARAKARANG BARU | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/18PPLchG8Fxraio7_bUzKal00rHQxZ2tWu_NODSnNhn8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Ies8lAx8df_Hsyo3-E-xiirDcgvhD1hz8ZSWqvG-LgI/edit?usp=drive_link | SUTT
PHT.46 | 46 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 5.6 | 2514 | GTACSR | 2X410 | 5.6 | 2514 | GTACSR | 2X410 | MUARAKARANG BARU | GIS MUARAKARANG BARU | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/18PPLchG8Fxraio7_bUzKal00rHQxZ2tWu_NODSnNhn8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1lBiXVwY0r9BSraQc-cDQn3CcjxtoQCIDp5xP2nIIfR8/edit?usp=drive_link | SUTT
PHT.47 | 47 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#1 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #1 | #1 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 9.87 | 925 | XLPE | 800 | 9.87 | 925 | XLPE | 800 | NEW SENAYAN | NEW SENAYAN | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1C-4TaxopscXoF8qD5OK1PRuVWljX3lG0S2YhsQlukbo/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1lGMff0B0Vx_cn1EmcOhgtwmeHA5UJMtK9UNM2Z8YKhU/edit?usp=drive_link | SKTT
PHT.48 | 48 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#2 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #2 | #2 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 9.87 | 925 | XLPE | 800 | 9.87 | 925 | XLPE | 800 | NEW SENAYAN | NEW SENAYAN | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1C-4TaxopscXoF8qD5OK1PRuVWljX3lG0S2YhsQlukbo/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1uKIjsZbKKW3vINvUVaxo7QdxAKOrLSs1K94710hJecw/edit?usp=drive_link | SKTT
PHT.49 | 49 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 5 | 920 | XLPE CU | 1X1000 | NEW SENAYAN | NEW SENAYAN | SENAYAN | SENAYAN | https://docs.google.com/spreadsheets/d/1llxzjbT0_J5N2LD08yYWYtrCisUHbbXbR4J8pTksiDI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1DktR8xxYTa8UgieS5NzFt7Qg96EbC4qfY_5b7-gC73I/edit?usp=drive_link | SKTT
PHT.50 | 50 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 5 | 920 | XLPE CU | 1X1000 | NEW SENAYAN | NEW SENAYAN | SENAYAN | SENAYAN | https://docs.google.com/spreadsheets/d/1llxzjbT0_J5N2LD08yYWYtrCisUHbbXbR4J8pTksiDI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/15gcmP5VjWWFc3MMiBgZv2QNc3XSUyvcaZkGMF2cYhxI/edit?usp=drive_link | SKTT
PHT.51 | 51 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.054 | 737 | XLPE CU | 1000 | 3.054 | 737 | XLPE CU | 1000 | NEW SENAYAN | NEW SENAYAN | ULUJAMI | ULUJAMI | https://docs.google.com/spreadsheets/d/1hfBRJz74yrGsdoW2pqFkUetEmLlimrUZaATZOmfFB68/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1MC6UbAz2f9O6ayqUHDH_g7iUjPQQI5-IdXThFVgCHns/edit?usp=drive_link | SKTT
PHT.52 | 52 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.054 | 737 | XLPE CU | 1000 | 3.054 | 737 | XLPE CU | 1000 | NEW SENAYAN | NEW SENAYAN | ULUJAMI | ULUJAMI | https://docs.google.com/spreadsheets/d/1hfBRJz74yrGsdoW2pqFkUetEmLlimrUZaATZOmfFB68/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1-IJaaTiettplWcaFkecHD5zfnswK8b_tCcnH3d7p_eY/edit?usp=drive_link | SKTT
PHT.53 | 53 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.36 | 2514 | GTACSR | 2X410 | 3.36 | 2514 | GTACSR | 2X410 | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | DAAN MOGOT | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1SuW0pJvmtnDnd4zy2Wnf_dZolx6WOa8vCwRnerM7dec/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1YGa_PVGzABwUO_XdoGaxHbpdee8b9otrhWySIYGOLU0/edit?usp=drive_link | SUTT
PHT.54 | 54 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.36 | 2514 | GTACSR | 2X410 | 3.36 | 2514 | GTACSR | 2X410 | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | DAAN MOGOT | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1SuW0pJvmtnDnd4zy2Wnf_dZolx6WOa8vCwRnerM7dec/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/13MdaR73iIKtJX5PAgkQ_ZbBPPp-y9QUKpFXvBcltxLw/edit?usp=drive_link | SUTT
PHT.55 | 55 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 5.6 | 2514 | GTACSR | 2X410 | 5.6 | 2514 | GTACSR | 2X410 | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | GIS MUARAKARANG BARU | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1GPjknpMV5K-h8nnmRxVQ6sgbCY2dnEfgqKJ7HGN2F34/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1RkCiSNWQAMb88zA5-RuysCadr4crMJJe0rn_5O97PwU/edit?usp=drive_link | SUTT
PHT.56 | 56 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 5.6 | 2514 | GTACSR | 2X410 | 5.6 | 2514 | GTACSR | 2X410 | PANTAI INDAH KAPUK | PANTAI INDAH KAPUK | GIS MUARAKARANG BARU | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1GPjknpMV5K-h8nnmRxVQ6sgbCY2dnEfgqKJ7HGN2F34/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1bzJMnzBNtFfjomWM7ESw7rkW_8ghzQDOzQFbVksZByg/edit?usp=drive_link | SUTT
PHT.57 | 57 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV TOMANG | PHT 150kV GROGOL #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.11 | 1191 | XLPE CU | 1x2000 | 4.11 | 1191 | XLPE CU | 1x2000 | TOMANG | TOMANG | GROGOL | GROGOL | https://docs.google.com/spreadsheets/d/1t7tKAqOObQgDhuC92b50M51QC3TXs2odrYNpv2H7BT0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1HSPLekve4h2FgfFw4r9w23Uh28rpQE0KBO38A1CCU6k/edit?usp=drive_link | SKTT
PHT.58 | 58 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV TOMANG | PHT 150kV GROGOL #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.11 | 1191 | XLPE CU | 1x2000 | 4.11 | 1191 | XLPE CU | 1x2000 | TOMANG | TOMANG | GROGOL | GROGOL | https://docs.google.com/spreadsheets/d/1t7tKAqOObQgDhuC92b50M51QC3TXs2odrYNpv2H7BT0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1fRlcSaCHamkAJa-kLVTsvRPdIe30kqNbHtcWboAD4Vc/edit?usp=drive_link | SKTT
PHT.59 | 59 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.054 | 737 | XLPE CU | 1000 | 3.054 | 737 | XLPE CU | 1000 | ULUJAMI | ULUJAMI | NEW SENAYAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/170Z7hWAGWx66QsbYbh6HO5MRELxgBPUJEyB4JBU2GTs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1bG5rOiNz_-liuI3ZWq6e9w0Pvo9SQmXx2tLZR0kWhyU/edit?usp=drive_link | SKTT
PHT.60 | 60 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.054 | 737 | XLPE CU | 1000 | 3.054 | 737 | XLPE CU | 1000 | ULUJAMI | ULUJAMI | NEW SENAYAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/170Z7hWAGWx66QsbYbh6HO5MRELxgBPUJEyB4JBU2GTs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1EHa-YQkKZlA61m19012MYQii-qV-p8Ktr5ULbtaWjp0/edit?usp=drive_link | SKTT
PHT.61 | 61 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | MUARAKARANG BARU | GISTET MUARAKARANG | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1ObTRHV1c0pdkrKfM1pvcvOgBzJLg3yhlj466L15T9ho/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/18zfpWH0vK84CS9EeyuCUVbranP1Onxw7d50n0ZfT2tU/edit?usp=drive_link | SUTET
PHT.62 | 62 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | MUARAKARANG BARU | GISTET MUARAKARANG | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1ObTRHV1c0pdkrKfM1pvcvOgBzJLg3yhlj466L15T9ho/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1oxan4y0FQIZgplW7ic3vnTaZnOW84GFRmO1fF9bNtgE/edit?usp=drive_link | SUTET
PHT.63 | 63 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | MUARAKARANG BARU | GISTET MUARAKARANG | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1ObTRHV1c0pdkrKfM1pvcvOgBzJLg3yhlj466L15T9ho/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1BfK_HajYZX8ks1L6JFY9oCN2m9qPEcjYXpr9qFUzH6c/edit?usp=drive_link | SUTET
PHT.64 | 64 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | MUARAKARANG BARU | GISTET MUARAKARANG | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1ObTRHV1c0pdkrKfM1pvcvOgBzJLg3yhlj466L15T9ho/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1-MyjOpotSCGEaWnns23yqX-OV3sWSEvkq5-Q2DE-NcA/edit?usp=drive_link | SUTET
PHT.65 | 65 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 |  |  | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | #1 | #VALUE! | #VALUE! | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | MUARAKARANG BARU | GISTET MUARAKARANG | TANJUNG PRIOK | TANJUNG PRIOK |  |  | SUTET
PHT.66 | 66 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 |  |  | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | #2 | #VALUE! | #VALUE! | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | MUARAKARANG BARU | GISTET MUARAKARANG | TANJUNG PRIOK | TANJUNG PRIOK |  |  | SUTET
PHT.67 | 67 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 |  |  | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | #1 | #VALUE! | #VALUE! | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | MUARAKARANG BARU | GISTET MUARAKARANG | TANJUNG PRIOK | TANJUNG PRIOK |  |  | SUTET
PHT.68 | 68 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 |  |  | 500 kV/100 V |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | #2 | #VALUE! | #VALUE! | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | MUARAKARANG BARU | GISTET MUARAKARANG | TANJUNG PRIOK | TANJUNG PRIOK |  |  | SUTET
PHT.69 | 69 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GI 150KV CURUG | PHT 150kV CIKUPA #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 18.655 | 1416 | XLPE CU | 2x1000 | CURUG | CURUG | CIKUPA | CIKUPA | https://docs.google.com/spreadsheets/d/15ManiJZ7SNsg5IdHnB5XdwKg1xUhDlHNkTeGFuUUNN4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1gS4R9JIPm3MxppUtT-afKiselL-PRe9Jkqt5ZeCir5Y/edit?usp=drive_link | SKTT
PHT.70 | 70 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#2 | 3200/1 | 3200/1 | 150 kV/100 V |  | GI 150KV CURUG | PHT 150kV CIKUPA #2 | #2 | 3200 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 18.655 | 1416 | XLPE CU | 2x1000 | CURUG | CURUG | CIKUPA | CIKUPA | https://docs.google.com/spreadsheets/d/15ManiJZ7SNsg5IdHnB5XdwKg1xUhDlHNkTeGFuUUNN4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/10XThA6g2zUyrvsbjt9c_Yb3G49qXwNzHaO3q8Fs15UI/edit?usp=drive_link | SKTT
PHT.71 | 71 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#1 | 3200/1 | 3200/1 | 150 kV/100 V |  | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #1 | #1 | 3200 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.7 | 1445 | XLPE CU | 2x1000 | 4.7 | 1445 | XLPE CU | 2x1000 | CURUG | CURUG | SUMMARECON GADING SERPONG | GADING SERPONG | https://docs.google.com/spreadsheets/d/1ChRppnBSdS__0hLBtoP_kp2e5gxgFEnJq6tVfqUTTGg/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/158xnn4VUt8rYrAHQ9dc9GJtu1bCtB_Xsf08oSfRmVDM/edit?usp=drive_link | SKTT
PHT.72 | 72 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.7 | 1445 | XLPE CU | 2x1000 | 4.7 | 1445 | XLPE CU | 2x1000 | CURUG | CURUG | SUMMARECON GADING SERPONG | GADING SERPONG | https://docs.google.com/spreadsheets/d/1ChRppnBSdS__0hLBtoP_kp2e5gxgFEnJq6tVfqUTTGg/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1y0BlikOs-AdK9euUH0YZjzEqA0eL3gT_xEwtq64uPRU/edit?usp=drive_link | SKTT
PHT.73 | 73 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | 2000/1 | 2000/1 | 150 kV/100 V |  | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST |  |  | 7.57 | 1620 | ZEBRA | 2X485 | 7.69 | 1620 | ZEBRA | 2X485 | GAJAH TUNGGAL | GAJAH TUNGGAL | PASAR KEMIS | PASAR KEMIS | https://docs.google.com/spreadsheets/d/189VyEvCtKkmAKhyJf7kBCJtOrZqlojmYR3jUKcSSx6c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/15M9aJzZzNu5hlgrMke4A-x8s0Bqc0Sw3YQzyredDJcI/edit?usp=drive_link | Hybrid
PHT.74 | 74 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | 2000/1 | 2000/1 | 150 kV/100 V |  | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 6.56 | 1620 | ZEBRA | 2X485 | 6.56 | 1620 | ZEBRA | 2X485 | GAJAH TUNGGAL | GAJAH TUNGGAL | PASAR KEMIS BARU | PASAR KEMIS BARU | https://docs.google.com/spreadsheets/d/1EkoIFE1lReMG0x4HAeestGiqqFxD4i0re0DhGL82Mio/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1kC70sE5aQrIpuxGujxYvzZvZXsJUypCKBD4qR5Hbgcc/edit?usp=drive_link | Hybrid
PHT.75 | 75 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV TANGERANG BARU | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV ITS | PHT 150kV TANGERANG BARU | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.99 | 3800 | ACCC Hamburg | 2x520 | 3.99 | 3800 | ACCC Hamburg | 2x520 | ITS | KTT ITS | TANGERANG BARU | TANGERANG BARU | https://docs.google.com/spreadsheets/d/1fTVsetrlPSeLXWz3Zgm5VzBf9-d-NGgnCMqcQyITBW0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/183f3r1m0S_cQEntotSm-DMYWR7td4P67IJDiI6E5k9U/edit?usp=sharing | SUTT
PHT.76 | 76 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV CENGKARENG BARU | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV ITS | PHT 150kV CENGKARENG BARU | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 2.39 | 3800 | ACCC Hamburg | 2x520 | 2.39 | 3800 | ACCC Hamburg | 2x520 | ITS | KTT ITS | CENGKARENG BARU | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1ETVBiTmF86Ikpxuywsmag6vacCFFu-lswkVJnkiSmJA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1aqNg3Mlr9twgz_hGmVOGxUwz9HbewC6tlkYDjQsfu9g/edit?usp=drive_link | Hybrid
PHT.77 | 77 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV KONSUMEN | 300/1 | 300/1 | 150 kV/100 V |  | GI 150KV ITS | PHT 150kV KONSUMEN | #1 | 300 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | No Data | 560 | XLPE CU | 1x300 | ITS | KTT ITS | KONSUMEN | KONSUMEN | https://docs.google.com/spreadsheets/d/1g2HZojHWh_GPIg8bK48t2QcWJ-TBfM-UQOP_MXmd6S0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1DSkWdSbfURDayk9UcU3AzxdzyZQ16FUv2rJ1ux90TLE/edit?usp=drive_link | SKTT
PHT.78 | 78 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#1 | 1600/5 | 1600/5 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV CIKUPA #1 | #1 | 1600 | 5 | 150 | 100 V | DIST |  |  | No Data | No Data | No Data | No Data | 7.2 | 1560 | ACSR DRAKE | 2x468 | JATAKE | JATAKE LAMA | CIKUPA | CIKUPA | https://docs.google.com/spreadsheets/d/1PscMJFHVgnw5U-HrfqCpmfimaqZgQ8mLbmMw2wLWXX8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/19rEhayqjtwaWSoT5ZTvIbc5k2NzuDDs1Laia6Fj-Nsc/edit?usp=drive_link | SUTT
PHT.79 | 79 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#2 | 1600/5 | 1600/5 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV CIKUPA #2 | #2 | 1600 | 5 | 150 | 100 V | DIST |  |  | No Data | No Data | No Data | No Data | 7.2 | 1560 | ACSR DRAKE | 2x468 | JATAKE | JATAKE LAMA | CIKUPA | CIKUPA | https://docs.google.com/spreadsheets/d/1PscMJFHVgnw5U-HrfqCpmfimaqZgQ8mLbmMw2wLWXX8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1vzC1yp74fxeW_SkTib1X3vUtPqKeRIPe4QzDFGSWtYE/edit?usp=drive_link | SUTT
PHT.80 | 80 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#1 | 1600/5 | 1600/5 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV JATAKE BARU #1 | #1 | 1600 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 3.12 | 1620 | ZEBRA | 2X484.5 | 3.12 | 1620 | ZEBRA | 2X484.5 | JATAKE | JATAKE LAMA | JATAKE BARU | JATAKE BARU | https://docs.google.com/spreadsheets/d/1cuwUvcfBw-sxCMQMiUw-wR6ED-fdrO9F1ne3pc0lnkI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1JeQl8fuBX8efnvZ36FsRC3KOBPdukfNMtC4OZXnd90s/edit?usp=drive_link | SUTT
PHT.81 | 81 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#2 | 1600/5 | 1600/5 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV JATAKE BARU #2 | #2 | 1600 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 3.12 | 1620 | ZEBRA | 2X484.5 | 3.12 | 1620 | ZEBRA | 2X484.5 | JATAKE | JATAKE LAMA | JATAKE BARU | JATAKE BARU | https://docs.google.com/spreadsheets/d/1cuwUvcfBw-sxCMQMiUw-wR6ED-fdrO9F1ne3pc0lnkI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1U4LNFfdRgkG3oTL8LS9vYsoJSOwmdYIxb6iZucimlf8/edit?usp=drive_link | SUTT
PHT.82 | 82 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | #1 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | JATAKE | JATAKE LAMA | MAXIMANGANDO | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1qGi39cl3Q5uqXHNw5o2PtWyNxKV_Ez7Cam22oXUaOr4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/15GsUKUcg8JFZFdO28Po0aIH7dQZTMd49pg75AzRjtqc/edit?usp=drive_link | SKTT
PHT.83 | 83 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | #2 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | JATAKE | JATAKE LAMA | MAXIMANGANDO | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1qGi39cl3Q5uqXHNw5o2PtWyNxKV_Ez7Cam22oXUaOr4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Aq7yTz8ADrd9gs4q9_ofm_8Fmb-bD8-uFGXMHXiPROk/edit?usp=drive_link | SKTT
PHT.84 | 84 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | #1 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | JATAKE | JATAKE LAMA | MAXIMANGANDO | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1qGi39cl3Q5uqXHNw5o2PtWyNxKV_Ez7Cam22oXUaOr4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/15GsUKUcg8JFZFdO28Po0aIH7dQZTMd49pg75AzRjtqc/edit?usp=drive_link | SKTT
PHT.85 | 85 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | #2 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | JATAKE | JATAKE LAMA | MAXIMANGANDO | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1qGi39cl3Q5uqXHNw5o2PtWyNxKV_Ez7Cam22oXUaOr4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Aq7yTz8ADrd9gs4q9_ofm_8Fmb-bD8-uFGXMHXiPROk/edit?usp=drive_link | SKTT
PHT.86 | 86 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | #1 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | MAXIMANGANDO | MAXIMANGANDO | JATAKE | JATAKE LAMA | https://docs.google.com/spreadsheets/d/19tKn_qEHN1BNhVr-JewSY5z7JpjqKKkhlWkT0gVXlWo/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/11n1GJXlqbL-fua2lnF0pUvVF-UHI58wZnqL0wpwUnJE/edit?usp=drive_link | SKTT
PHT.87 | 87 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | #2 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | MAXIMANGANDO | MAXIMANGANDO | JATAKE | JATAKE LAMA | https://docs.google.com/spreadsheets/d/19tKn_qEHN1BNhVr-JewSY5z7JpjqKKkhlWkT0gVXlWo/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Y0-J-8ad6pziDYgoE37bzaxqgoc9kqSEsFjNgaD3L7A/edit?usp=drive_link | SKTT
PHT.88 | 88 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | #1 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | MAXIMANGANDO | MAXIMANGANDO | JATAKE | JATAKE LAMA | https://docs.google.com/spreadsheets/d/19tKn_qEHN1BNhVr-JewSY5z7JpjqKKkhlWkT0gVXlWo/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/11n1GJXlqbL-fua2lnF0pUvVF-UHI58wZnqL0wpwUnJE/edit?usp=drive_link | SKTT
PHT.89 | 89 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | #2 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 1.1 | 1000 | XLPE CU | 1x1000 | 1.1 | 1000 | XLPE CU | 1x1000 | MAXIMANGANDO | MAXIMANGANDO | JATAKE | JATAKE LAMA | https://docs.google.com/spreadsheets/d/19tKn_qEHN1BNhVr-JewSY5z7JpjqKKkhlWkT0gVXlWo/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Y0-J-8ad6pziDYgoE37bzaxqgoc9kqSEsFjNgaD3L7A/edit?usp=drive_link | SKTT
PHT.90 | 90 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 7.1 | 2648 | TACSR | 2x480.86 | SINDANG JAYA | SINDANG JAYA | BALARAJA | BALARAJA | https://docs.google.com/spreadsheets/d/1hiJXuJrxl0OvdosMZDPvzHLNT9ZBbLp-6W3STqgLaF8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1IK2DYZcHm5MkukKyo1x7sG4osnO77byJ3aebcjgBbsQ/edit?usp=drive_link | SUTT
PHT.91 | 91 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 7.1 | 2648 | TACSR | 2x480.86 | SINDANG JAYA | SINDANG JAYA | BALARAJA | BALARAJA | https://docs.google.com/spreadsheets/d/1hiJXuJrxl0OvdosMZDPvzHLNT9ZBbLp-6W3STqgLaF8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/15gdVi4iRgc364cz2LCPXPoymgaYb-bXkYVqk5pMWfhs/edit?usp=drive_link | SUTT
PHT.92 | 92 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 12.53 | 2648 | TACSR | 2X410 | 12.53 | 2648 | TACSR | 2X410 | SINDANG JAYA | SINDANG JAYA | LONTAR | PLTU LONTAR | https://docs.google.com/spreadsheets/d/1ErV0jbkzE3r9Lwzqug5IE4dJgHOge4q6JJtLt_HHjt0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1U-e69FkdoUL2MHWdFa_2hYYwWbYENik7Czn_T0sXlm8/edit?usp=drive_link | SUTT
PHT.93 | 93 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 12.53 | 2648 | TACSR | 2X410 | 12.53 | 2648 | TACSR | 2X410 | SINDANG JAYA | SINDANG JAYA | LONTAR | PLTU LONTAR | https://docs.google.com/spreadsheets/d/1ErV0jbkzE3r9Lwzqug5IE4dJgHOge4q6JJtLt_HHjt0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1qwiSHMFlcv5bowRY0YFSepceEHpXtH9gAImbRim5Et4/edit?usp=drive_link | SUTT
PHT.94 | 94 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 4.13 | 2648 | TACSR | 2x480.86 | SINDANG JAYA | SINDANG JAYA | SUVARNA SUTERA | SUVARNA SUTERA | https://docs.google.com/spreadsheets/d/1lBUKaJ4srEprs0En4vURaOQSZnDNLol6us4GP8gL2p4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1O4iMK9fq5D-Ra0BlxdvdxrAQVSVgmVroY1RpVxIVvxk/edit?usp=drive_link | SUTT
PHT.95 | 95 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 4.13 | 2648 | TACSR | 2x480.86 | SINDANG JAYA | SINDANG JAYA | SUVARNA SUTERA | SUVARNA SUTERA | https://docs.google.com/spreadsheets/d/1lBUKaJ4srEprs0En4vURaOQSZnDNLol6us4GP8gL2p4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1zgS9FZQl2jleL4mQE63ZxZbLXZjVl3s33lWSd_btP9I/edit?usp=drive_link | SUTT
PHT.96 | 96 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #1 | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 21.23 | 2648 | TACSR | 2X410 | 21.23 | 2648 | TACSR | 2X410 | TANGERANG BARU | TANGERANG BARU | LONTAR | PLTU LONTAR | https://docs.google.com/spreadsheets/d/10fRiHsxsfAtI_ZQLPJ5DD2rfZCETcvNnOcyvoEFJEIY/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1DThmS_TVshKSUqPXvHlRCDS8SSllAv9njZSdiiIxYzA/edit?usp=drive_link | SUTT
PHT.97 | 97 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#2 | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #2 | #2 | 3000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 21.23 | 2648 | TACSR | 2X410 | 21.23 | 2648 | TACSR | 2X410 | TANGERANG BARU | TANGERANG BARU | LONTAR | PLTU LONTAR | https://docs.google.com/spreadsheets/d/10fRiHsxsfAtI_ZQLPJ5DD2rfZCETcvNnOcyvoEFJEIY/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1XrLp-G8k7jH4zGHSxyHG0NR2ILCmpE7qbBrtiIPAO50/edit?usp=drive_link | SUTT
PHT.98 | 98 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV ITS | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV TANGERANG BARU | PHT 150kV ITS | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 3.99 | 3800 | ACCC Hamburg | 2x520 | 3.99 | 3800 | ACCC Hamburg | 2x520 | TANGERANG BARU | TANGERANG BARU | ITS | KTT ITS | https://docs.google.com/spreadsheets/d/1luzvY5n3Pc85zc_5AAkVFpnlbnJmOoST5y3pB85ItEE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1it9FF1xe83IbwSASHWr6oaErJsEriRUqQaS56v-8wJI/edit?usp=sharing | SUTT
PHT.99 | 99 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV CENGKARENG BARU | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 6.3 | 3800 | ACCC Hamburg | 2x520 | 6.3 | 3800 | ACCC Hamburg | 2x520 | TANGERANG BARU | TANGERANG BARU | CENGKARENG BARU | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1MmKKnhiS1_bSxujX-o7ChAvUzKdF0ASLszVhnbFYd5I/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1j9UPZUhHwjANqFfmzKGm3xEdGXc1O7eyNWCa34mR_Ho/edit?usp=drive_link | Hybrid
PHT.100 | 100 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV TELUK NAGA | PHT 150kV DADAP #1 | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 6.132 | 2648 | TACSR | 2X410 | 6.132 | 2648 | TACSR | 2X410 | TELUK NAGA | TELUK NAGA | DADAP | DADAP | https://docs.google.com/spreadsheets/d/198WYUPTADUBT8LiTPL55K5-W-N3wMg4rQ79gQ5aWbd0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1YIxxO10MIvc8tyb1gtdpGEiZdlhWW1RuxusmJ2kgMWk/edit?usp=drive_link | SUTT
PHT.101 | 101 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#2 | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV TELUK NAGA | PHT 150kV DADAP #2 | #2 | 3000 | 1 | 150 | 100 V | LCD+DIST | Eksternal |  | 6.132 | 2648 | TACSR | 2X410 | 6.132 | 2648 | TACSR | 2X410 | TELUK NAGA | TELUK NAGA | DADAP | DADAP | https://docs.google.com/spreadsheets/d/198WYUPTADUBT8LiTPL55K5-W-N3wMg4rQ79gQ5aWbd0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1z7IEr0_A4Qi-QOKuYJdiDxj_6tXWqtlKbaN-WPlrQSc/edit?usp=drive_link | SUTT
PHT.102 | 102 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#1 | 1600/1 | 1600/1 | 150 kV/100 V |  | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #1 | #1 | 1600 | 1 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 9.17 | 1620 | ZEBRA | 2X484.5 | TELUK NAGA | TELUK NAGA | SEPATAN | SEPATAN | https://docs.google.com/spreadsheets/d/1tQr5q--sYIs6INvcIfPqvjCXM3YjZF_DgqgVNi1YA4U/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1ktTfifoI-vKO265I_tJpjGjERcLVVWM0vTqYn7dHHz0/edit?usp=drive_link | SUTT
PHT.103 | 103 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#2 | 1600/1 | 1600/1 | 150 kV/100 V |  | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #2 | #2 | 1600 | 1 | 150 | 100 V | LCD+DIST | Internal |  | No Data | No Data | No Data | No Data | 9.17 | 1620 | ZEBRA | 2X484.5 | TELUK NAGA | TELUK NAGA | SEPATAN | SEPATAN | https://docs.google.com/spreadsheets/d/1tQr5q--sYIs6INvcIfPqvjCXM3YjZF_DgqgVNi1YA4U/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1yDYsqFIpydB6CDBSYEp9OYWIaUX7Qsm0ROMrl7QLxuE/edit?usp=drive_link | SUTT
PHT.104 | 104 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.12 | 1620 | ZEBRA | 2X484.5 | 3.12 | 1620 | ZEBRA | 2X484.5 | JATAKE BARU | JATAKE BARU | JATAKE | JATAKE LAMA | https://docs.google.com/spreadsheets/d/14853UNkib_CBux3g0N3JoyTbws77__htzIEiE4Fdi6c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/13ZV4tc5EeW_qFPs7NnfQ2SjrrN8e_QqBhLSaJPdzk6g/edit?usp=drive_link | SUTT
PHT.105 | 105 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 3.12 | 1620 | ZEBRA | 2X484.5 | 3.12 | 1620 | ZEBRA | 2X484.5 | JATAKE BARU | JATAKE BARU | JATAKE | JATAKE LAMA | https://docs.google.com/spreadsheets/d/14853UNkib_CBux3g0N3JoyTbws77__htzIEiE4Fdi6c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1lBAwbE9vWR6-QkBtTryO638VTZndtaM_wGX5y9820pQ/edit?usp=drive_link | SUTT
PHT.106 | 106 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 6.37 | 1620 | ZEBRA | 2X484.5 | 6.37 | 1620 | ZEBRA | 2X484.5 | JATAKE BARU | JATAKE BARU | TANGERANG | TANGERANG LAMA | https://docs.google.com/spreadsheets/d/1twSTDrzJ0khbVYOnymVwG01XOR021fVNqxEqSsTHMU4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1HFvkvO46ebK0mXTuH1HXRgQR220W2IwVUMjfwdwWwC0/edit?usp=drive_link | SUTT
PHT.107 | 107 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 6.37 | 1620 | ZEBRA | 2X484.5 | 6.37 | 1620 | ZEBRA | 2X484.5 | JATAKE BARU | JATAKE BARU | TANGERANG | TANGERANG LAMA | https://docs.google.com/spreadsheets/d/1twSTDrzJ0khbVYOnymVwG01XOR021fVNqxEqSsTHMU4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1c5pCIMYCr_m4Ih5QsIqFUlh0E-R6Xkney5ZWW5CibeA/edit?usp=drive_link | SUTT
PHT.108 | 108 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #1 | #1 | 4000 | 1 | 150 | 100 V | DIST | Eksternal |  | 12.53 | 2648 | TACSR | 2X410 | 12.53 | 2648 | TACSR | 2X410 | LONTAR | PLTU LONTAR | SINDANG JAYA | SINDANG JAYA | https://docs.google.com/spreadsheets/d/1VpUt5FtKDRaGE1XgAnjESg_GXpPbmGJ5oKWynUpNi8M/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Mad--6xOYKdlWz7byYqWgJJ2U-IDHngdf14uvAKoHyk/edit?usp=drive_link | SUTT
PHT.109 | 109 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #2 | #2 | 4000 | 1 | 150 | 100 V | DIST | Eksternal |  | 12.53 | 2648 | TACSR | 2X410 | 12.53 | 2648 | TACSR | 2X410 | LONTAR | PLTU LONTAR | SINDANG JAYA | SINDANG JAYA | https://docs.google.com/spreadsheets/d/1VpUt5FtKDRaGE1XgAnjESg_GXpPbmGJ5oKWynUpNi8M/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1r7qBDETtEcGGFVwKJvmQXfFoCOcMy-x_xN0dXZsT5MY/edit?usp=drive_link | SUTT
PHT.110 | 110 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV LONTAR | PHT 150kV DADAP #1 | #1 | 3000 | 1 | 150 | 100 V | DIST | Eksternal |  | 26.271 | 2648 | TACSR | 2X410 | 26.271 | 2648 | TACSR | 2X410 | LONTAR | PLTU LONTAR | DADAP | DADAP | https://docs.google.com/spreadsheets/d/1QT5J4LpiCd14zivWKzfbr7haaYxPypko5YD95TKdat8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1_n9Zp7Y2NoT_qqHqUVK3QLyxdX4QlC3zjlX8DHlFcy0/edit?usp=drive_link | SUTT
PHT.111 | 111 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#2 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV LONTAR | PHT 150kV DADAP #2 | #2 | 3000 | 1 | 150 | 100 V | DIST | Eksternal |  | 26.271 | 2648 | TACSR | 2X410 | 26.271 | 2648 | TACSR | 2X410 | LONTAR | PLTU LONTAR | DADAP | DADAP | https://docs.google.com/spreadsheets/d/1QT5J4LpiCd14zivWKzfbr7haaYxPypko5YD95TKdat8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/16N_hQUDTAm-C31zmw9FvHAx4H116toI10NQHsNfMECA/edit?usp=drive_link | SUTT
PHT.112 | 112 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #1 | #1 | 3000 | 1 | 150 | 100 V | DIST | Eksternal |  | 21.23 | 2648 | TACSR | 2X410 | 21.23 | 2648 | TACSR | 2X410 | LONTAR | PLTU LONTAR | TANGERANG BARU | TANGERANG BARU | https://docs.google.com/spreadsheets/d/1L1Fcl03-F7UeQHcUbbS3kZH7V8agFXBGzK9geklidIk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1GK01xt7hoqWLkwpSKVVMm3hH1gWFgjsGNpxPWiTE3es/edit?usp=drive_link | SUTT
PHT.113 | 113 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#2 | 3000/1 | 3000/1 | 150 kV/100 V |  | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #2 | #2 | 3000 | 1 | 150 | 100 V | DIST | Eksternal |  | 21.23 | 2648 | TACSR | 2X410 | 21.23 | 2648 | TACSR | 2X410 | LONTAR | PLTU LONTAR | TANGERANG BARU | TANGERANG BARU | https://docs.google.com/spreadsheets/d/1L1Fcl03-F7UeQHcUbbS3kZH7V8agFXBGzK9geklidIk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/16vozHIoxHVT0qgs6hajKPjl1Z7aNoJy71doFQVnw1co/edit?usp=drive_link | SUTT
PHT.114 | 114 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 10.32 | 1600 | TACSR 520 | 587.3 | 10.32 | 1600 | TACSR 520 | 587.3 | CENGKARENG | CENGKARENG LAMA | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/19OF0tf0ckZpdaglHmakyEpJZ8JoateArcknWBuciWO4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Ww0Df6e_JdVjjcwy_b2eezckHonTWQ-IdRlbOe5HyMI/edit?usp=drive_link | SUTT
PHT.115 | 115 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 10.32 | 1600 | TACSR 520 | 587.3 | 10.32 | 1600 | TACSR 520 | 587.3 | CENGKARENG | CENGKARENG LAMA | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/19OF0tf0ckZpdaglHmakyEpJZ8JoateArcknWBuciWO4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1QUT6oi3kKdCYExcT1xM-NcNSsZ0oFRc9vPIlOoAwGZA/edit?usp=drive_link | SUTT
PHT.116 | 116 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#1 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #1 | #1 | 4000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.4 | 4000 | XLPE CU | 2x2000 | 0.4 | 4000 | XLPE CU | 2x2000 | CENGKARENG | CENGKARENG LAMA | CENGKARENG BARU | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1sSFmSN__YlV9ZiMcd_o4nVF4I5mOAROHnspn-T607sI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/13dqZROd78XDCm2sGvj4Xk-DGTIpsIokV60v4XNI-RxI/edit?usp=drive_link | SKTT
PHT.117 | 117 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#2 | 3000/5 | 3000/5 | 150 kV/100 V |  | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #2 | #2 | 3000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.4 | 4000 | XLPE CU | 2x2000 | 0.4 | 4000 | XLPE CU | 2x2000 | CENGKARENG | CENGKARENG LAMA | CENGKARENG BARU | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1sSFmSN__YlV9ZiMcd_o4nVF4I5mOAROHnspn-T607sI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1JZKV5Er1VvbzG3V4qGwYW__IxmqcaY9PcJlYJ3nx0dU/edit?usp=drive_link | SKTT
PHT.118 | 118 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV CENGKARENG | PHT 150kV TANGERANG #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 9.468 | 1250 | ACCC Lisbon | 1x310 | 9.468 | 1250 | ACCC Lisbon | 1x310 | CENGKARENG | CENGKARENG LAMA | TANGERANG | TANGERANG LAMA | https://docs.google.com/spreadsheets/d/1V5oXmxuQJDs6hVUhllFsQWSAczR9qDVizcWKUQAxC8c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1hMhfYciYCyp6nppuMwlWI0AgiOB2ycLbQyc1toMrvVA/edit?usp=drive_link | SUTT
PHT.119 | 119 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV CENGKARENG | PHT 150kV TANGERANG #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 9.468 | 1250 | ACCC Lisbon | 1x310 | 9.468 | 1250 | ACCC Lisbon | 1x310 | CENGKARENG | CENGKARENG LAMA | TANGERANG | TANGERANG LAMA | https://docs.google.com/spreadsheets/d/1V5oXmxuQJDs6hVUhllFsQWSAczR9qDVizcWKUQAxC8c/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/18jqihAmmeb2YC5TZsLMIy1aWMYLf-AeSuu5MZ9oHZ_Q/edit?usp=drive_link | SUTT
PHT.120 | 120 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#1 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #1 | #1 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | No Data | 738 | NA2XCK2Y | 1x1000 | CENGKARENG BARU | CENGKARENG BARU | BANDARA SOEKARNO HATTA | KONSUMEN BANDARA | https://docs.google.com/spreadsheets/d/1hsTTD3sEZ6p_q8ry1hhf-X2Z8FeQL-3qSGjeJTLrHLk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1EkKq7YMaHRlfUW5Swjcx_w5QxNJkVmtLd-tOb3UCuwk/edit?usp=drive_link | SKTT
PHT.121 | 121 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#2 | 1000/1 | 1000/1 | 150 kV/100 V |  | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #2 | #2 | 1000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | No Data | 738 | NA2XCK2Y | 1x1000 | CENGKARENG BARU | CENGKARENG BARU | BANDARA SOEKARNO HATTA | KONSUMEN BANDARA | https://docs.google.com/spreadsheets/d/1hsTTD3sEZ6p_q8ry1hhf-X2Z8FeQL-3qSGjeJTLrHLk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1OvlR6HmEdqGju8L5nGM4xZtiFr_YodYcBzsyiLyxnuw/edit?usp=drive_link | SKTT
PHT.122 | 122 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.4 | 4000 | XLPE CU | 2x2000 | 0.4 | 4000 | XLPE CU | 2x2000 | CENGKARENG BARU | CENGKARENG BARU | CENGKARENG | CENGKARENG LAMA | https://docs.google.com/spreadsheets/d/1cmUMRcNL3m3GlfS5kFt9glmj7pj69GZKx2axiu_F6EE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1HXicHZIQ-GaHmPJoF8vtEUceUxVAoEQiqCSAlFHGUrA/edit?usp=drive_link | SKTT
PHT.123 | 123 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#2 | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #2 | #2 | 4000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 0.4 | 4000 | XLPE CU | 2x2000 | 0.4 | 4000 | XLPE CU | 2x2000 | CENGKARENG BARU | CENGKARENG BARU | CENGKARENG | CENGKARENG LAMA | https://docs.google.com/spreadsheets/d/1cmUMRcNL3m3GlfS5kFt9glmj7pj69GZKx2axiu_F6EE/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1yfy5JZXISpMVw-R3sugttS_dRI-Hx6azWvD1B-sZDCI/edit?usp=drive_link | SKTT
PHT.124 | 124 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV ITS | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV CENGKARENG BARU | PHT 150kV ITS | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 2.39 | 3800 | ACCC Hamburg | 2x520 | 2.39 | 3800 | ACCC Hamburg | 2x520 | CENGKARENG BARU | CENGKARENG BARU | ITS | KTT ITS | https://docs.google.com/spreadsheets/d/1eMaVMiMWfZXnX6iJ77Rs50hxRK5sauLLyQ6rC5coSxM/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1TON7JqybXDQqv5vep4Ymt07iau7ilPQK1o_I-t6yI8o/edit?usp=drive_link | Hybrid
PHT.125 | 125 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV TANGERANG BARU | 4000/1 | 4000/1 | 150 kV/100 V |  | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Internal |  | 6.3 | 3800 | ACCC Hamburg | 2x520 | 6.3 | 3800 | ACCC Hamburg | 2x520 | CENGKARENG BARU | CENGKARENG BARU | TANGERANG BARU | TANGERANG BARU | https://docs.google.com/spreadsheets/d/1QTr7YxXBmNQSOVuywGPWAgZUjU8epsjsIMhExB47CTs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/187-jnRs8IP1RBfMsN8Deaa19nu7R9MTbl6LW4Way4Lk/edit?usp=drive_link | Hybrid
PHT.126 | 126 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#1 | 3000/1 | 3000/1 | 150 kV/100 V |  | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #1 | #1 | 3000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.25 | 1428 | XLPE CU | 2x1000 | 3.25 | 1428 | XLPE CU | 2x1000 | CILEDUG | CILEDUG | ALAM SUTERA | ALAMSUTERA | https://docs.google.com/spreadsheets/d/1qJJgA7C8VJIpm5DuGDSmbuP4x-FK7dB4iTdPZBS6OKA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1qN3MTSsZnLG3qoJeJFPXVcBHA3Dub-C1AzliJvcwRiw/edit?usp=drive_link | SKTT
PHT.127 | 127 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.25 | 1428 | XLPE CU | 2x1000 | 3.25 | 1428 | XLPE CU | 2x1000 | CILEDUG | CILEDUG | ALAM SUTERA | ALAMSUTERA | https://docs.google.com/spreadsheets/d/1qJJgA7C8VJIpm5DuGDSmbuP4x-FK7dB4iTdPZBS6OKA/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1y_xOr_sxzk3LIPrpPEqdRzcuSHy-FasJkN1wOD-g8M0/edit?usp=drive_link | SKTT
PHT.128 | 128 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#1 | 3200/1 | 3200/1 | 150 kV/100 V |  | GI 150KV CILEDUG | PHT 150kV METLAND #1 | #1 | 3200 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 5.36 | 1378 | XLPE CU | 2x1000 | 5.36 | 1378 | XLPE CU | 2x1000 | CILEDUG | CILEDUG | METLAND | METLAND | https://docs.google.com/spreadsheets/d/1mwjz98g6_M8PGcdZI2bv4F1TtH-jdZO1HFHx-6g-MK0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1ju8zrULuJkIKPGtaIk07pjwv4dk_2KLfGRBcCPJn5H0/edit?usp=drive_link | SKTT
PHT.129 | 129 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GI 150KV CILEDUG | PHT 150kV METLAND #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 5.36 | 1378 | XLPE CU | 2x1000 | 5.36 | 1378 | XLPE CU | 2x1000 | CILEDUG | CILEDUG | METLAND | METLAND | https://docs.google.com/spreadsheets/d/1mwjz98g6_M8PGcdZI2bv4F1TtH-jdZO1HFHx-6g-MK0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1iSOMAut5iinyns6FiHrDFv6I9zmGMSbvnura3yLC7Aw/edit?usp=drive_link | SKTT
PHT.130 | 130 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST |  |  | 10.32 | 1600 | TACSR 520 | 587.3 | 10.32 | 1600 | TACSR 520 | 587.3 | DURIKOSAMBI | DURIKOSAMBI | CENGKARENG | CENGKARENG LAMA | https://docs.google.com/spreadsheets/d/1e9cWuBvufXKB1JvvQ1r0GrZLb5rseZad8N8zoBv8Yt4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/12gem_gMMrXhnbHhl0jNwMG1RQDewmRvv9KzYA2Gwz7o/edit?usp=drive_link | SUTT
PHT.131 | 131 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST |  |  | 10.32 | 1600 | TACSR 520 | 587.3 | 10.32 | 1600 | TACSR 520 | 587.3 | DURIKOSAMBI | DURIKOSAMBI | CENGKARENG | CENGKARENG LAMA | https://docs.google.com/spreadsheets/d/1e9cWuBvufXKB1JvvQ1r0GrZLb5rseZad8N8zoBv8Yt4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1XHeabcATmoiXzbczrISnDosADc7FLjSsKrEqPhYAPXI/edit?usp=drive_link | SUTT
PHT.132 | 132 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV LMK | 1000/5 | 1000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV LMK | #1 | 1000 | 5 | 150 | 100 V | DIST |  |  | 0.3 | 780 | DRAKE | 1x468.5 | 0.3 | 780 | DRAKE | 1x468.5 | DURIKOSAMBI | DURIKOSAMBI | LMK | LMK | https://docs.google.com/spreadsheets/d/1si3Vh1XOiSrPiNXH0EITM3w2LTR2yCply6HfPXi8nng/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1OY291k7zDt6-eBiPIDrU8ww1TUMC9eLceEZx5LmCJY8/edit?usp=drive_link | SUTT
PHT.133 | 133 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#1 | 1600/5 | 1600/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #1 | #1 | 1600 | 5 | 150 | 100 V | LCD+DIST | Eksternal |  | 6.14 | 1600 | ACSR | 2x485 | 6.14 | 1600 | ACSR | 2x485 | DURIKOSAMBI | DURIKOSAMBI | GROGOL BARU | GROGOL BARU | https://docs.google.com/spreadsheets/d/1H22scBQwbDlPqxd5cQ0mO63Rju6cVsMth61-7vI5O4Q/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1QzJPlrFj79drqDLs5dDCiJUchmUilWCCDucJv-SEK7c/edit?usp=drive_link | SUTT
PHT.134 | 134 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#2 | 1600/5 | 1600/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #2 | #2 | 1600 | 5 | 150 | 100 V | LCD+DIST | Eksternal |  | 6.14 | 1600 | ACSR | 2x485 | 6.14 | 1600 | ACSR | 2x485 | DURIKOSAMBI | DURIKOSAMBI | GROGOL BARU | GROGOL BARU | https://docs.google.com/spreadsheets/d/1H22scBQwbDlPqxd5cQ0mO63Rju6cVsMth61-7vI5O4Q/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/19Tta_Pgf8VceaAZbcgvL0zsjdPRefgPXwJDHrSeTZmw/edit?usp=drive_link | SUTT
PHT.135 | 135 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#1 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #1 | #1 | 4000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 10.2 | 920 | CU | 800 | 10.2 | 920 | CU | 800 | DURIKOSAMBI | DURIKOSAMBI | KEBON JERUK | KEBON JERUK | https://docs.google.com/spreadsheets/d/1Ag7e6g3O11qK8wS8PtiJqUCeEJvXaIVhpJIrm5lb1ME/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/139OjcSqWTXj4CMRzKc1diiAOWKn-VyltKPQWtqG5c5E/edit?usp=drive_link | SKTT
PHT.136 | 136 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 10.2 | 920 | CU | 800 | 10.2 | 920 | CU | 800 | DURIKOSAMBI | DURIKOSAMBI | KEBON JERUK | KEBON JERUK | https://docs.google.com/spreadsheets/d/1Ag7e6g3O11qK8wS8PtiJqUCeEJvXaIVhpJIrm5lb1ME/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1oAq-UZ6qwvZAzGsVZiPZV6ZKqYY8WWNk875yfpl75LM/edit?usp=drive_link | SKTT
PHT.137 | 137 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#1 | 1000/5 | 1000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #1 | #1 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 6.84 | 920 | CU | 800 | 6.84 | 920 | CU | 800 | DURIKOSAMBI | DURIKOSAMBI | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1pw1pjZJtFfcJbSFJ_6Aj76BFipSNIudwLsLA6Xf5r84/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1oe8ujMX_JkOGE_FO4BV0bOCyLh1uOKWT9sSxtYehSV4/edit?usp=drive_link | SKTT
PHT.138 | 138 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#2 | 1000/5 | 1000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #2 | #2 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 6.84 | 920 | CU | 800 | 6.84 | 920 | CU | 800 | DURIKOSAMBI | DURIKOSAMBI | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1pw1pjZJtFfcJbSFJ_6Aj76BFipSNIudwLsLA6Xf5r84/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1OrmBeE4PMXy4O0pfhkM3858KR7KEvptf74AklLTRUKU/edit?usp=drive_link | SKTT
PHT.139 | 139 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#1 | 3000/5 | 3000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #1 | #1 | 3000 | 5 | 150 | 100 V | LCD+DIST |  |  | 2.63 | 2514 | GTACSR | 2X410 | 2.63 | 2514 | GTACSR | 2X410 | DURIKOSAMBI | DURIKOSAMBI | DAAN MOGOT | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1L8Ay-PlTjiTe4NPncXtXxZLADncpwLc6v-5-oWfAF10/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1p3nXTV53M5HPzYrRfyiqmUNPrTQsI37swmSfllTyM5Y/edit?usp=drive_link | SUTT
PHT.140 | 140 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#2 | 4000/5 | 4000/5 | 150 kV/100 V |  | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #2 | #2 | 4000 | 5 | 150 | 100 V | LCD+DIST |  |  | 2.63 | 2514 | GTACSR | 2X410 | 2.63 | 2514 | GTACSR | 2X410 | DURIKOSAMBI | DURIKOSAMBI | DAAN MOGOT | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1L8Ay-PlTjiTe4NPncXtXxZLADncpwLc6v-5-oWfAF10/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1AQJHBJ3OULojzO979M0lmk6fExy2VRM0dQY2KNNRlrk/edit?usp=drive_link | SUTT
PHT.141 | 141 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV TANGERANG | PHT 150kV CENGKARENG #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 9.468 | 1250 | ACCC Lisbon | 1x310 | 9.468 | 1250 | ACCC Lisbon | 1x310 | TANGERANG | TANGERANG LAMA | CENGKARENG | CENGKARENG LAMA | https://docs.google.com/spreadsheets/d/1-nwNPdfDOMCTNUYWn2bQhQKKgAHu_X_xBccDAOJNwgQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1WDQtAVRWVcMBXEYNrTaze76UdxxwbbtRifsBtPVoLfE/edit?usp=drive_link | SUTT
PHT.142 | 142 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV TANGERANG | PHT 150kV CENGKARENG #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 9.468 | 1250 | ACCC Lisbon | 1x310 | 9.468 | 1250 | ACCC Lisbon | 1x310 | TANGERANG | TANGERANG LAMA | CENGKARENG | CENGKARENG LAMA | https://docs.google.com/spreadsheets/d/1-nwNPdfDOMCTNUYWn2bQhQKKgAHu_X_xBccDAOJNwgQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1doRtkPD9VDq8BogaGbLM6VHPATJ25QnPRsghj_ox_Jc/edit?usp=drive_link | SUTT
PHT.143 | 143 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 6.37 | 1620 | ZEBRA | 2X484.5 | 6.37 | 1620 | ZEBRA | 2X484.5 | TANGERANG | TANGERANG LAMA | JATAKE BARU | JATAKE BARU | https://docs.google.com/spreadsheets/d/15c3jbuQdsQaonu5RjU5A4m_SV6rKno4E5GgtFOu5db4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1kLS7j2k8e3kLE9juhB96sMb6rlJJCvcUG1V-o0urseU/edit?usp=drive_link | SUTT
PHT.144 | 144 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 6.37 | 1620 | ZEBRA | 2X484.5 | 6.37 | 1620 | ZEBRA | 2X484.5 | TANGERANG | TANGERANG LAMA | JATAKE BARU | JATAKE BARU | https://docs.google.com/spreadsheets/d/15c3jbuQdsQaonu5RjU5A4m_SV6rKno4E5GgtFOu5db4/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1P5Pa3Gc7z8qCCGEBMA8aaHbBDhOp7gU8hFN4iD2QPTg/edit?usp=drive_link | SUTT
PHT.145 | 145 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#1 | 4000/1 | 4000/1 | 150 kV/100 V |  | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #1 | #1 | 4000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.25 | 1428 | XLPE CU | 2x1000 | 3.25 | 1428 | XLPE CU | 2x1000 | ALAM SUTERA | ALAMSUTERA | CILEDUG | CILEDUG | https://docs.google.com/spreadsheets/d/1K2mOtqHak_uQiinUoriiIU_vMiCg1XwzA2RAL-kFP4E/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1JchLGM_8JGuJ2UJzWXbOd_34ffbV58XmDC4FQaoDEjw/edit?usp=drive_link | SKTT
PHT.146 | 146 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 3.25 | 1428 | XLPE CU | 2x1000 | 3.25 | 1428 | XLPE CU | 2x1000 | ALAM SUTERA | ALAMSUTERA | CILEDUG | CILEDUG | https://docs.google.com/spreadsheets/d/1K2mOtqHak_uQiinUoriiIU_vMiCg1XwzA2RAL-kFP4E/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1mN0pVb9fDYDO035ti54lDmQmiSVbFuze2mvEuH3uui4/edit?usp=drive_link | SKTT
PHT.147 | 147 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 6.8 | 1510.64 | XLPE CU | 2x1000 | ALAM SUTERA | ALAMSUTERA | SUMMARECON GADING SERPONG | GADING SERPONG | https://docs.google.com/spreadsheets/d/1HBiP8a805GjIqh1w7_RkbLHztiTvkHsZXO2h6F77Q6E/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1gAeuD7_hhenIiw6X-N4CzMGpDDdgqFXuWll6Xg-r-fU/edit?usp=drive_link | SKTT
PHT.148 | 148 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 6.8 | 1510.64 | XLPE CU | 2x1000 | ALAM SUTERA | ALAMSUTERA | SUMMARECON GADING SERPONG | GADING SERPONG | https://docs.google.com/spreadsheets/d/1HBiP8a805GjIqh1w7_RkbLHztiTvkHsZXO2h6F77Q6E/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1lfft6hnMraU0pzLBcTbd3Ilop914Sdx_QEoqrEMglk8/edit?usp=drive_link | SKTT
PHT.149 | 149 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#1 | 3200/5 | 3200/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV METLAND #1 | #1 | 3200 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 2.609 | 1378 | XLPE CU | 2x1000 | 2.609 | 1378 | XLPE CU | 2x1000 | KEMBANGAN | KEMBANGAN | METLAND | METLAND | https://docs.google.com/spreadsheets/d/1UaakkQaz9NfIQc7_0C9HlaSK9urz2qn7NUtLVpgiKBw/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/19nEK6VrdppxmpRcAmCTt8rKTmgYKyWNNGtkXSIdXHSg/edit?usp=drive_link | SKTT
PHT.150 | 150 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#2 | 3200/5 | 3200/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV METLAND #2 | #2 | 3200 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 2.609 | 1378 | XLPE CU | 2x1000 | 2.609 | 1378 | XLPE CU | 2x1000 | KEMBANGAN | KEMBANGAN | METLAND | METLAND | https://docs.google.com/spreadsheets/d/1UaakkQaz9NfIQc7_0C9HlaSK9urz2qn7NUtLVpgiKBw/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1NANLIITCPB2AS9A4bNKUEYQCK53VaAY8s-AKxthNW2A/edit?usp=drive_link | SKTT
PHT.151 | 151 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#1 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #1 | #1 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 6.84 | 920 | CU | 800 | 6.84 | 920 | CU | 800 | KEMBANGAN | KEMBANGAN | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1vKSCzkzSKIO3hmwInCzMkhjACffQVOYXlo95L4rT2VI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/167url0Bt7IuvsrwV3Wlt9uVQ-XMxTkI90p4S6ymZSlo/edit?usp=drive_link | SKTT
PHT.152 | 152 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#2 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #2 | #2 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 6.84 | 920 | CU | 800 | 6.84 | 920 | CU | 800 | KEMBANGAN | KEMBANGAN | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1vKSCzkzSKIO3hmwInCzMkhjACffQVOYXlo95L4rT2VI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/10N9GvgG9WxD1cMlm7VmLlzCOnnOdRyQ-HerOmnYTI_s/edit?usp=drive_link | SKTT
PHT.153 | 153 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#1 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #1 | #1 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 9.87 | 925 | XLPE | 800 | 9.87 | 925 | XLPE | 800 | KEMBANGAN | KEMBANGAN | NEW SENAYAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1mW-HcOAxdUb9H_o49sGfaRqJhC5nbbIigvhI8mIPyTk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1WKkODzeTLuKPPCL6z-OrPXqu14ChOAqt0CYzkiR76pM/edit?usp=drive_link | SKTT
PHT.154 | 154 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#2 | 1000/5 | 1000/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #2 | #2 | 1000 | 5 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 9.87 | 925 | XLPE | 800 | 9.87 | 925 | XLPE | 800 | KEMBANGAN | KEMBANGAN | NEW SENAYAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1mW-HcOAxdUb9H_o49sGfaRqJhC5nbbIigvhI8mIPyTk/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1KpBWwyrMVRSi2zJV0aTTMb7s8_MI9zGmDUd10HaFGcs/edit?usp=drive_link | SKTT
PHT.155 | 155 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#1 | 2000/5 | 2000/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #1 | #1 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 7.12 | 2514 | GTACSR | 2X410 | 7.12 | 2514 | GTACSR | 2X410 | KEMBANGAN | KEMBANGAN | PETUKANGAN | PETUKANGAN | https://docs.google.com/spreadsheets/d/1rGqFdHcjgDn-87DRfvPu0KMLqd0viYPHZFUKDOcT_4Q/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1t31_j4b_xKzqeXfrqTvB4JKvS1t73HS8y7kAAWPio5w/edit?usp=drive_link | Hybrid
PHT.156 | 156 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#2 | 2000/5 | 2000/5 | 150 kV/100 V |  | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #2 | #2 | 2000 | 5 | 150 | 100 V | LCD+DIST | Internal |  | 7.12 | 2514 | GTACSR | 2X410 | 7.12 | 2514 | GTACSR | 2X410 | KEMBANGAN | KEMBANGAN | PETUKANGAN | PETUKANGAN | https://docs.google.com/spreadsheets/d/1rGqFdHcjgDn-87DRfvPu0KMLqd0viYPHZFUKDOcT_4Q/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1zmIRITbtSDzGzlGqLszJtZFF3WSEBbEZ-yVWIca5FcI/edit?usp=drive_link | Hybrid
PHT.157 | 157 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV METLAND | PHT 150kV KEMBANGAN #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 2.609 | 1378 | XLPE CU | 2x1000 | 2.609 | 1378 | XLPE CU | 2x1000 | METLAND | METLAND | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1AgdFYyxANPQzbn_rWbbCYz6EJL49zHh_y2rEp9bplnQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/179_CH1lkXiKt-J1FguRux5erjkhXOw1ivyXQjf9OZbg/edit?usp=drive_link | SKTT
PHT.158 | 158 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV METLAND | PHT 150kV KEMBANGAN #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 2.609 | 1378 | XLPE CU | 2x1000 | 2.609 | 1378 | XLPE CU | 2x1000 | METLAND | METLAND | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1AgdFYyxANPQzbn_rWbbCYz6EJL49zHh_y2rEp9bplnQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Cjyd2jz0C-e2Dwbb_jPFq1_UZiZcvp5FintVJFAL4q8/edit?usp=drive_link | SKTT
PHT.159 | 159 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV METLAND | PHT 150kV CILEDUG #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 5.36 | 1378 | XLPE CU | 2x1000 | 5.36 | 1378 | XLPE CU | 2x1000 | METLAND | METLAND | CILEDUG | CILEDUG | https://docs.google.com/spreadsheets/d/1FRw841eWNccHEuAbMYlx7TrMqJqxs80QRm6Bw1qybac/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1VEww-qRd52g7ojdAmLqyodaxK6VH3YTHkO81Ssy7KFM/edit?usp=drive_link | SKTT
PHT.160 | 160 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV METLAND | PHT 150kV CILEDUG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 5.36 | 1378 | XLPE CU | 2x1000 | 5.36 | 1378 | XLPE CU | 2x1000 | METLAND | METLAND | CILEDUG | CILEDUG | https://docs.google.com/spreadsheets/d/1FRw841eWNccHEuAbMYlx7TrMqJqxs80QRm6Bw1qybac/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1bZ9XHIPIKVQQrKIzDS1Zvo5UXruEg1dK4wxT5CiejFs/edit?usp=drive_link | SKTT
PHT.161 | 161 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 6.8 | 1510.64 | XLPE CU | 2x1000 | SUMMARECON GADING SERPONG | GADING SERPONG | ALAM SUTERA | ALAMSUTERA | https://docs.google.com/spreadsheets/d/1jRglYVR6VX3Xweu7l9q-TfqBrbdOaCOyQBtJgzTFxjQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/114A2IquyW1w_Elx655JgkryY-P1CmKq6elV4me_qcfw/edit?usp=drive_link | SKTT
PHT.162 | 162 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | No Data | No Data | No Data | No Data | 6.8 | 1510.64 | XLPE CU | 2x1000 | SUMMARECON GADING SERPONG | GADING SERPONG | ALAM SUTERA | ALAMSUTERA | https://docs.google.com/spreadsheets/d/1jRglYVR6VX3Xweu7l9q-TfqBrbdOaCOyQBtJgzTFxjQ/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1KWa9-PZ8g1_KvdAUqxqErVkca4WdxXGNVzL2ebE0Cpo/edit?usp=drive_link | SKTT
PHT.163 | 163 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#1 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #1 | #1 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.7 | 1445 | XLPE CU | 2x1000 | 4.7 | 1445 | XLPE CU | 2x1000 | SUMMARECON GADING SERPONG | GADING SERPONG | CURUG | CURUG | https://docs.google.com/spreadsheets/d/1QkoIMG5VpmmRkfC_q1Vr1YHpRlB-BLfzAt3WQsPEWSs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1b89Yr8Sb190GQEFnO6G5zemn5Ku4ehDsvs7xwiBoSMc/edit?usp=drive_link | SKTT
PHT.164 | 164 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#2 | 2000/1 | 2000/1 | 150 kV/100 V |  | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #2 | #2 | 2000 | 1 | 150 | 100 V | LCD+DIST | Tidak Aktif |  | 4.7 | 1445 | XLPE CU | 2x1000 | 4.7 | 1445 | XLPE CU | 2x1000 | SUMMARECON GADING SERPONG | GADING SERPONG | CURUG | CURUG | https://docs.google.com/spreadsheets/d/1QkoIMG5VpmmRkfC_q1Vr1YHpRlB-BLfzAt3WQsPEWSs/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/19Al_PWI0Qw-CKb9WkhT3jHx0EY8L_6bgvAY0Rt5HkAY/edit?usp=drive_link | SKTT
PHT.165 | 165 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | GANDUL | GANDUL | https://docs.google.com/spreadsheets/d/1IeEeidfUufsg2hFIqd3vUjxYGVqDIsnPDA3zkQ9MNV0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/19botCaaavxDBaf-vARrZlUhyojcuz9Rbbh_3pnyAtjE/edit?usp=drive_link | SUTET
PHT.166 | 166 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/14xMP0JFvWjj6KeCRRfUaJD77P7MlwQt1JgTT5bHF6a8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/11BV33oYcBclStuVCuJZ7V96PSV7fhb_zHswq3X7Z2Io/edit?usp=drive_link | SUTET
PHT.167 | 167 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | MUARAKARANG | GISTET MUARAKARANG | https://docs.google.com/spreadsheets/d/1P7OYKmXYmn75ZCAlLkfKYLkW6aaVTeL1FnCl-uBFc4Y/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/14AlF79AraBJTeGh9qkIwk3s73H_7xgfBZyKW8Pwv9ns/edit?usp=drive_link | SUTET
PHT.168 | 168 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | MUARAKARANG | GISTET MUARAKARANG | https://docs.google.com/spreadsheets/d/1P7OYKmXYmn75ZCAlLkfKYLkW6aaVTeL1FnCl-uBFc4Y/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1dzxuS-kaeIJKCwYQctaWZz4BLbJCilVkltEeraPu1d0/edit?usp=drive_link | SUTET
PHT.169 | 169 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | GANDUL | GANDUL | https://docs.google.com/spreadsheets/d/1IeEeidfUufsg2hFIqd3vUjxYGVqDIsnPDA3zkQ9MNV0/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1qoEK7SsH6Gy9AeMYtLG1S3L3Tnqz4qTUu2Axm6lwaoE/edit?usp=drive_link | SUTET
PHT.170 | 170 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | KEMBANGAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/14xMP0JFvWjj6KeCRRfUaJD77P7MlwQt1JgTT5bHF6a8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1d_AKQc0gJyCAP-iRNKw2R-DeEPn-Yz7-7oaCY3nEewA/edit?usp=drive_link | SUTET
PHT.171 | 171 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | MUARAKARANG | GISTET MUARAKARANG | https://docs.google.com/spreadsheets/d/1P7OYKmXYmn75ZCAlLkfKYLkW6aaVTeL1FnCl-uBFc4Y/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/16rxOCvaN_bd9qM1Pwedxa2TICeufOdtdjf2Vsd9RMcg/edit?usp=drive_link | SUTET
PHT.172 | 172 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | 11.168 | 5980 | ACSR/AS 450 | 4x492.5 | DURIKOSAMBI | DURIKOSAMBI | MUARAKARANG | GISTET MUARAKARANG | https://docs.google.com/spreadsheets/d/1P7OYKmXYmn75ZCAlLkfKYLkW6aaVTeL1FnCl-uBFc4Y/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1l3DP_rtaIzlRxs49FWFlXOqB3M1q9iRdnGOS8iYSPRA/edit?usp=drive_link | SUTET
PHT.173 | 173 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1K_c7GmuObfmcASkw3oks-uQUpoWKPtz-IGeEeHr-maI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1E1ypR8s3N8wv1w3IrqS3cErlpvXo_TK3H_PDwmd-Dhk/edit?usp=drive_link | SUTET
PHT.174 | 174 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1K_c7GmuObfmcASkw3oks-uQUpoWKPtz-IGeEeHr-maI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/19fOcmB5XJClL6YUBYhyUzFlL8Q2bYuiKm-mpqiXpKmI/edit?usp=drive_link | SUTET
PHT.175 | 175 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | 47.2 | 4052 | ACSR/AS 450 | 4x492,5 | KEMBANGAN | KEMBANGAN | BALARAJA | BALARAJA | https://docs.google.com/spreadsheets/d/1I0QVrwQMtb5zkpn-yI30KtKyKUB47OacA2Ul0KsQvd8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/14lQs5k6qf3O2swxH6HfjlTvqF_WgmJSAdpS-rJdRj_U/edit?usp=drive_link | SUTET
PHT.176 | 176 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | 47.2 | 4052 | ACSR/AS 450 | 4x492,5 | KEMBANGAN | KEMBANGAN | BALARAJA | BALARAJA | https://docs.google.com/spreadsheets/d/1I0QVrwQMtb5zkpn-yI30KtKyKUB47OacA2Ul0KsQvd8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1Vw3_-zf-Ka1O5vV0kmLORYNd18vCxnySllxGtUJVQIU/edit?usp=drive_link | SUTET
PHT.177 | 177 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | 2000/1 | 2000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | #1 | 2000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | GANDUL | GANDUL | https://docs.google.com/spreadsheets/d/1DMb2Xdjfs2Hnvtaq3DZV6F0uSOGqPrJ4fPXkYoaU6ko/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1WjPj7DDPLm96jjJtSsM-UfYyQXnLVY6ifcBsJvG4F5Q/edit?usp=drive_link | SUTET
PHT.178 | 178 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | 2000/1 | 2000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | #2 | 2000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | GANDUL | GANDUL | https://docs.google.com/spreadsheets/d/1DMb2Xdjfs2Hnvtaq3DZV6F0uSOGqPrJ4fPXkYoaU6ko/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1WjPj7DDPLm96jjJtSsM-UfYyQXnLVY6ifcBsJvG4F5Q/edit?usp=drive_link | SUTET
PHT.179 | 179 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1K_c7GmuObfmcASkw3oks-uQUpoWKPtz-IGeEeHr-maI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1P-3QKmuQg1MlHPY7ElDPJs6wpZuxCryWU1_mN8mpfng/edit?usp=drive_link | SUTET
PHT.180 | 180 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | 3.943 | 3224 | ACSR/AS 450 (16 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | DURIKOSAMBI | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1K_c7GmuObfmcASkw3oks-uQUpoWKPtz-IGeEeHr-maI/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1MdZ6Enr6Y2q97JgUB9rThQurVRGjooKTns1xEaxtN7E/edit?usp=drive_link | SUTET
PHT.181 | 181 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | #1 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | 47.2 | 4052 | ACSR/AS 450 | 4x492,5 | KEMBANGAN | KEMBANGAN | BALARAJA | BALARAJA | https://docs.google.com/spreadsheets/d/1I0QVrwQMtb5zkpn-yI30KtKyKUB47OacA2Ul0KsQvd8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1wCwDFJw1G5416feNkOtOGu-M8US49ozY3izaUqroNSM/edit?usp=drive_link | SUTET
PHT.182 | 182 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | 4000/1 | 4000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | #2 | 4000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | No Data | No Data | No Data | No Data | 47.2 | 4052 | ACSR/AS 450 | 4x492,5 | KEMBANGAN | KEMBANGAN | BALARAJA | BALARAJA | https://docs.google.com/spreadsheets/d/1I0QVrwQMtb5zkpn-yI30KtKyKUB47OacA2Ul0KsQvd8/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1RfqRnc2Jhl0Y7bVuY9D3GW9iy9SNbg3jPmqU5fFCaAQ/edit?usp=drive_link | SUTET
PHT.183 | 183 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | 2000/1 | 2000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | #1 | 2000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | GANDUL | GANDUL | https://docs.google.com/spreadsheets/d/1DMb2Xdjfs2Hnvtaq3DZV6F0uSOGqPrJ4fPXkYoaU6ko/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1RQQoBbTf6BB1zJJy3Tv0m3ZIQD7fQpwRUIMkuh2oK2w/edit?usp=drive_link | SUTET
PHT.184 | 184 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | 2000/1 | 2000/1 | 500 kV/100 V |  | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | #2 | 2000 | 1 | 500 | 100 V | LCD+DIST | Eksternal |  | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | 30.1 | 3224 | ACSR/AS 450 (16 Tower) ACSR GANNET (89 Tower) | 4x492.5 | KEMBANGAN | KEMBANGAN | GANDUL | GANDUL | https://docs.google.com/spreadsheets/d/1DMb2Xdjfs2Hnvtaq3DZV6F0uSOGqPrJ4fPXkYoaU6ko/edit?usp=drive_link | https://docs.google.com/spreadsheets/d/1RQQoBbTf6BB1zJJy3Tv0m3ZIQD7fQpwRUIMkuh2oK2w/edit?usp=drive_link | SUTET

## LCD
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | SIRKIT | RATIO CT - MPU | RATIO PT | RELAY | HELPER ASET |  | MERK | TIPE | NO. SERI | JENIS RELE | TH OPERASI | LCD | [14 empty] | LCD
[9 empty] | GI/GIS | BAY | [5 empty] | TAP SET | SETTING CURRENT DIFF | [13 empty] | SET RELAY | SETTING CURRENT DIFF
[17 empty] | Line Imp | Line Angle | In | Is1 | Is2 | k1 | k2 | Firmware | Komunikasi (Direct/Mux) | Supervisi Idiff | Starter Diff | Starter ISEF | PDF | TGL |  | Source : Form Implementasi Scanning
[32 empty] | Line Imp | Line Angle | In | Is1 | Is2 | k1 | k2 | Firmware | Komunikasi (Direct/Mux) | Supervisi Idiff | Starter Diff | Starter ISEF | FILE | km
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46
PHT.01 | 1 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV ANCOL #1 | GE | MICOM P545 | 36039274/03/22 | NUMERIK | 2022 |  | 0.329 | 70.066 | 5 | 1 | 10 | 30 | 150 | [5 empty] | 35. [Approved] LCD_546_ANGKE BAY ANCOL 1,2.pdf | 2022-08-29 |  | 0.33 | 70 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 4.6
PHT.02 | 2 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV ANCOL #2 | GE | MICOM P545 | 36039272/03/22 | NUMERIK | 2022 |  | 0.329 | 70.066 | 5 | 1 | 10 | 30 | 150 | [5 empty] | 35. [Approved] LCD_546_ANGKE BAY ANCOL 1,2.pdf | 2022-08-29 |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.03 | 3 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KARET LAMA #1 | GE | MICOM P443 | 34424435/04/18 | NUMERIK | 2019 |  | 0 | 0 | 5 | N/A | N/A | - | - | [8 empty] | 1.296 | 78 | 5 | N/A | N/A | - | - | [6 empty] | 7.9
PHT.04 | 4 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KARET LAMA #2 | GE | MICOM P443 | 34424434/04/18 | NUMERIK | 2019 |  | 0 | 0 | 5 | N/A | N/A | - | - | [8 empty] | 1.296 | 78 | 5 | N/A | N/A | - | - | [6 empty] | 7.9
PHT.05 | 5 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KETAPANG #1 | ALSTOM | MICOM P545 | 34421606/04/18 | NUMERIK | 2021 |  | 0.064 | 56.6 | 5 | 1 | 10 | 30 | 150 | [5 empty] | Tap Setting Official Angke-Ketapang dan arah sebaliknya.pdf | 2019-03-06 |  | 0.244 | 82 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 5.5
PHT.06 | 6 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KETAPANG #2 | ALSTOM | MICOM P545 | 34421607/04/18 | NUMERIK | 2021 |  | 0.064 | 56.6 | 5 | 1 | 10 | 30 | 150 | [5 empty] | Tap Setting Official Angke-Ketapang dan arah sebaliknya.pdf | 2019-03-06 |  | 0.232 | 57 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 5.5
PHT.07 | 7 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #1 | SIEMENS | 7SD61 | BF0807106719 | NUMERIK | 2018 |  | 0.468 | 57.296 | 5 | 10.2 | 102 | - | - | [5 empty] | Tap Setting Official GI Angke bay OHL Muarakarang Lama 1,2-1.pdf | 2019-09-04 |  | 0 | 0 | 5 | 1 | 10 | - | - | [6 empty] | 0
PHT.08 | 8 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #2 | SIEMENS | 7SD61 | BF0807106718 | NUMERIK | 2018 |  | 0.468 | 57.296 | 5 | 10.2 | 102 | - | - | [5 empty] | Tap Setting Official GI Angke bay OHL Muarakarang Lama 1,2-1.pdf | 2019-09-04 |  | 0 | 0 | 5 | 1 | 10 | - | - | [6 empty] | 0
PHT.09 | 9 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #1 | SIEMENS | 7SL87 | BM1712005923 | NUMERIK | 2018 |  | 0.125 | 81.357 | 5 | 1 | 10 | - | - | [5 empty] | Rev.01 MKLMA-ANGKE dan Sebaliknya.pdf | 2018-12-14 |  | 0 | 0 | 5 | 0 | 0 | - | - | [6 empty] | 0
PHT.10 | 10 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #2 | SIEMENS | 7SL87 | BM1712005927 | NUMERIK | 2018 |  | 0.125 | 81.357 | 5 | 1 | 10 | - | - | [5 empty] | Rev.01 MKLMA-ANGKE dan Sebaliknya.pdf | 2018-12-14 |  | 0 | 0 | 5 | 0 | 0 | - | - | [6 empty] | 0
PHT.11 | 11 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV LONTAR #1 | GE | MICOM P446 | 34465139/05/18 | NUMERIK | 2021 |  | 19.398 | 82.725 | 1 | N/A | N/A | - | - | [5 empty] | 20200220_Dadap - Lontar 1_2.pdf | 2020-02-20 |  | 19.92 | 83 | 1 | N/A | N/A | - | - | [6 empty] | 26.26
PHT.12 | 12 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV LONTAR #2 | GE | MICOM P446 | 34465154/05/18 | NUMERIK | 2021 |  | 19.398 | 82.725 | 1 | N/A | N/A | - | - | [5 empty] | 20200220_Dadap - Lontar 1_2.pdf | 2020-02-20 |  | 19.92 | 83 | 1 | N/A | N/A | - | - | [6 empty] | 26.26
PHT.13 | 13 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV TELUK NAGA #1 | GE | MICOM P546 | 34465138/05/18 | NUMERIK | 2021 |  | 4.649 | 82.725 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 20200220_Dadap - Teluk Naga 1_2.pdf | 2020-02-20 |  | 4.65 | 83 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.13
PHT.14 | 14 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV TELUK NAGA #2 | GE | MICOM P546 | 34465149/05/18 | NUMERIK | 2021 |  | 4.649 | 82.725 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 20200220_Dadap - Teluk Naga 1_2.pdf | 2020-02-20 |  | 4.65 | 83 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.13
PHT.15 | 15 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 2500/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #1 | ALSTOM | MICOM P545 | 34923699/11/19 | NUMERIK |  |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [8 empty] | 0.014 | 73 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 0.26
PHT.16 | 16 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 2500/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #2 | ALSTOM | MICOM P545 | 32197930/06/12 | NUMERIK |  |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [8 empty] | 0.014 | 73 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 0.26
PHT.17 | 17 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #1 | AREVA | MICOM P521 | 1307744 | NUMERIK |  |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [5 empty] | 2026 01 12 Resetting MKRBR-MKRLM rev 1.pdf | 2026-01-12 |  | 0 | 0 | 5 | 0.2 | 2 | 30 | 150 | [6 empty] | 0
PHT.18 | 18 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #2 | ALSTOM | MICOM P543 | 31995324/12/11 | NUMERIK |  |  | 0.2 | 82 | 5 | 1.5 | 5 | 30 | 150 | [8 empty] | 0.2 | 82 | 5 | 1.5 | 5 | 30 | 150 | [6 empty] | 0.7
PHT.19 | 19 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #1 | SIEMENS | 7SD61 | BF0807106717 | NUMERIK | 2019 |  | 0.468 | 57.296 | 5 | 10.2 | 102 | - | - | [5 empty] | Tap Setting Official GI Muarakarang Lama bay OHL Angke 1,2.pdf | 2019-08-30 |  | 0 | 0 | 5 | 1 | 10 | - | - | [6 empty] | 0
PHT.20 | 20 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #2 | SIEMENS | 7SD61 | BF0807106723 | NUMERIK | 2019 |  | 0.468 | 57.296 | 5 | 10.2 | 102 | - | - | [5 empty] | Tap Setting Official GI Muarakarang Lama bay OHL Angke 1,2.pdf | 2019-08-30 |  | 0 | 0 | 5 | 1 | 10 | - | - | [6 empty] | 0
PHT.21 | 21 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#1 | #1 | 1200/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #1 | GE | MICOM P546 | 37123537/07/25 | NUMERIK | 2026 |  | 0.26 | 72.87 | 5 | 0.61 | 6.13 | 30 | 80 | [5 empty] | (OFFICIAL)TAP SETTING MUARAKARANG LAMA - BUDI KEMULIAAN 1 DAN 2 MICOM P545-546.pdf | 2025-10-08 |  | 0.26 | 72.87 | 5 | 0.61 | 6.13 | 30 | 80 | [6 empty] | 14
PHT.22 | 22 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#2 | #2 | 1200/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #2 | GE | MICOM P546 | 37362776/03/26 | NUMERIK | 2026 |  | 0.26 | 72.87 | 5 | 0.61 | 6.13 | 30 | 80 | [5 empty] | (OFFICIAL)TAP SETTING MUARAKARANG LAMA - BUDI KEMULIAAN 1 DAN 2 MICOM P545-546.pdf | 2025-10-08 |  | 0.26 | 72.87 | 5 | 0.61 | 6.13 | 30 | 80 | [6 empty] | 14
PHT.23 | 23 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #1 | AREVA | MICOM P521 | 1307747 | NUMERIK |  |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [5 empty] | 2026 01 12 Resetting MKRLM-MKRBR rev 1.pdf | 2026-01-12 |  | 0 | 0 | 5 | 0.5 | 1 | 60 | 150 | [6 empty] | 0
PHT.24 | 24 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #2 | AREVA | MICOM P543 | 31507153/09/10 | NUMERIK |  |  | 0.2 | 82 | 5 | 3 | 5 | 30 | 150 | [8 empty] | 0.2 | 82 | 5 | 3 | 5 | 30 | 150 | [6 empty] | 0.7
PHT.25 | 25 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #1 | SIEMENS | 7SL87 | BM1712005935 | NUMERIK | 2018 |  | 0.125 | 81.357 | 5 | 10.2 | 102 | - | - | [5 empty] | Rev.01 MKLMA-ANGKE dan Sebaliknya.pdf | 2018-12-14 |  | 0.0333 | 81.36 | 5 | 1 | 10 | - | - | [6 empty] | 3.6
PHT.26 | 26 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #2 | SIEMENS | 7SL87 | BM1712005931 | NUMERIK | 2018 |  | 0.125 | 81.357 | 5 | 10.2 | 102 | - | - | [5 empty] | Rev.01 MKLMA-ANGKE dan Sebaliknya.pdf | 2018-12-14 |  | 0.0333 | 81.36 | 5 | 1 | 10 | - | - | [6 empty] | 3.6
PHT.27 | 27 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #1 | ABB | RED670 | T1645093 | NUMERIK | 2019 |  | 2.591 | N/A | 1 | 0.2 | 1 | 30 | 80 | [5 empty] | official tap setting proteksi sutt daan mogot - durikosambi 1,2_rev01.pdf | 2019-08-28 |  | 0 | N/A | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.28 | 28 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #2 | ABB | RED670 | T1645092 | NUMERIK | 2019 |  | 2.591 | N/A | 1 | 0.2 | 1 | 30 | 80 | [5 empty] | official tap setting proteksi sutt daan mogot - durikosambi 1,2_rev01.pdf | 2019-08-28 |  | 0 | N/A | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.29 | 29 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #1 | ALSTOM | MICOM P545 | 32197932/07/12 | NUMERIK | 2022 |  | 11.484 | 81.3 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | official tap setting proteksi sutt daan mogot - pik 1,2.pdf | 2019-07-31 |  | 11.48 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.6
PHT.30 | 30 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #2 | ALSTOM | MICOM P545 | 34164813/08/17 | NUMERIK | 2019 |  | 11.484 | 81.3 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | official tap setting proteksi sutt daan mogot - pik 1,2.pdf | 2019-07-31 |  | 11.48 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.6
PHT.31 | 31 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#1 | #1 | 1600/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #1 | SIEMENS | 7SL87 | BM1809009341 | NUMERIK | 2019 |  | 0.299 | 82 | 1 |  | 2 | - | - | [5 empty] | Official Grogol-Grogol II.pdf | 2019-10-23 |  | 0.299 | 82 | 1 | 0.2 | 2 | - | - | [6 empty] | 2
PHT.32 | 32 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#2 | #2 | 1600/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #2 | SIEMENS | 7SL87 | BM1909000269 | NUMERIK | 2020 |  | 0.299 | 82 | 1 |  | 2 | - | - | [5 empty] | Official Grogol-Grogol II.pdf | 2019-10-23 |  | 0.299 | 82 | 1 | 0.2 | 2 | - | - | [6 empty] | 2
PHT.33 | 33 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV TOMANG #1 | SCHNEIDER | MICOM P543 | 753937F | NUMERIK | 2021 |  | 0.831 | 85 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | official tap setting LCD, DIST, OCR grogol - tomang 1,2.pdf | 2019-10-31 |  | 0.83 | 85 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 4.11
PHT.34 | 34 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV TOMANG #2 | SCHNEIDER | MICOM P543 | 753791F | NUMERIK | 2021 |  | 0.831 | 85 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | official tap setting LCD, DIST, OCR grogol - tomang 1,2.pdf | 2019-10-31 |  | 0.83 | 85 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.11
PHT.35 | 35 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #1 | SIEMENS | 7SL87 | BM1804005484 | NUMERIK | 2019 |  | 0.374 | 82 | 1 |  | 2 | - | - | [5 empty] | Official Grogol II - Durikosambi.pdf | 2019-10-23 |  | 0.374 | 82 | 1 | 0.2 | 2 | - | - | [6 empty] | 6.468
PHT.36 | 36 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #2 | SIEMENS | 7SL87 | BM1804005475 | NUMERIK | 2020 |  | 0.374 | 82 | 1 |  | 2 | - | - | [5 empty] | Official Grogol II - Durikosambi.pdf | 2019-10-23 |  | 0.374 | 82 | 1 | 0.2 | 2 | - | - | [6 empty] | 6.468
PHT.37 | 37 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #1 | SIEMENS | 7SL87 | BM1804005481 | NUMERIK | 2019 |  | 0.374 | 82 | 1 |  | 2 | - | - | [5 empty] | Official Grogol II - Grogol.pdf | 2019-10-23 |  | 0.374 | 82 | 1 | 0.2 | 2 | - | - | [6 empty] | 2
PHT.38 | 38 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #2 | SIEMENS | 7SL87 | BM1804005478 | NUMERIK | 2020 |  | 0.374 | 82 | 1 |  | 2 | - | - | [5 empty] | Official Grogol II - Grogol.pdf | 2019-10-23 |  | 0.374 | 82 | 1 | 0.2 | 2 | - | - | [6 empty] | 2
PHT.39 | 39 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #1 | ALSTOM | MICOM P545 | 34665002/12/18 | NUMERIK | 2019 |  | 0.156 | 72 | 5 | 1.5 | 10 | 30 | 150 | [5 empty] | 2021 10 22 - Rev02.Tap Setting GIS Kebon Jeruk bay Durikosambi 1,2.pdf | 2021-10-22 |  | 4.275 | 57 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 5.4
PHT.40 | 40 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #2 | ALSTOM | MICOM P545 | 34482258/06/18 | NUMERIK | 2019 |  | 0.16 | 71.57 | 5 | 1.5 | 9.2 | 30 | 80 | [5 empty] | DAFTAR SETELAN RELAI PROTEKSI GIS 150kV KEBONJERUK_07.04.26.pdf | 2026-04-07 |  | 4.68 | 72 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 10.2
PHT.41 | 41 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#1 | #1 | 500/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #1 | ALSTOM | MICOM P545 | 34923727/11/19 | NUMERIK | 2020 |  | 0 | 0 | 5 | 1.5 | 10 | 30 | 150 | [5 empty] | 21 10 22 - Rev02.Tap Setting GIS Kebon Jeruk bay Karet 2.pdf | 2021-10-22 |  | 8.55 | 57 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 5.4
PHT.42 | 42 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#2 | #2 | 500/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #2 | ALSTOM | MICOM P545 | 34485202/06/18 | NUMERIK | 2020 |  | 0 | 0 | 5 | 1.5 | 10 | 30 | 150 | [5 empty] | 21 10 22 - Rev02.Tap Setting GIS Kebon Jeruk bay Karet 2.pdf | 2021-10-22 |  | 0.57 | 57 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 5.4
PHT.43 | 43 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #1 | ALSTOM | MICOM P545 | 34724838/02/19 | NUMERIK | 2022 |  | 0.051 | 72.903 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | Copy of UGC GIS Muarakarang Baru - Mkarang Baru (AIS) Sirkit 1_LCD P545_OCR P142_rev01.pdf | 2021-10-01 |  | 0.05 | 73 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 0.26
PHT.44 | 44 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #2 | ALSTOM | MICOM P545 | 34724836/02/19 | NUMERIK | 2022 |  | 0.043 | 72.903 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | Copy of UGC GIS Muarakarang Baru - Mkarang Baru (AIS) Sirkit 2_LCD P545_OCR P142_rev01.pdf | 2021-09-01 |  | 0.05 | 73 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 0.26
PHT.45 | 45 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #1 | ALSTOM | MICOM P545 | 34724837/02/19 | NUMERIK | 2022 |  | 15.822 | 81.296 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | GIS MUARAKARANG BARU BAY PIK 1,2.PDF | 2022-04-13 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.46 | 46 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #2 | ALSTOM | MICOM P545 | 34724835/02/19 | NUMERIK | 2022 |  | 15.822 | 81.296 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | GIS MUARAKARANG BARU BAY PIK 1,2.PDF | 2022-04-13 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.47 | 47 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #1 | GE | MICOM P546 | 37132771/07/25 | NUMERIK | 2025 |  | 0.15 | 72.87 | 5 | 0.93 | 9.25 | 30 | 80 | [5 empty] | (Official) NEW SENAYAN - KEMBANGAN 1 DAN 2 - TAP MICOM P545-546_Revisi 1.pdf | 2025-11-05 |  | 0.15 | 72.87 | 5 | 0.93 | 9.25 | 30 | 80 | [6 empty] | 9.87
PHT.48 | 48 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #2 | GE | MICOM P546 | 37132773/07/25 | NUMERIK | 2025 |  | 0.15 | 72.87 | 5 | 0.93 | 9.25 | 30 | 80 | [5 empty] | (Official) NEW SENAYAN - KEMBANGAN 1 DAN 2 - TAP MICOM P545-546_Revisi 1.pdf | 2025-11-05 |  | 0.15 | 72.87 | 5 | 0.93 | 9.25 | 30 | 80 | [6 empty] | 9.87
PHT.49 | 49 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #1 | ALSTOM | MICOM P545 | 33493424/11/15 | NUMERIK | 2019 |  | 0.118 | 84 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | Rev.02 NewSenayan-Senayan1,2 (1).pdf | 2019-11-14 |  | 0.12 | 84 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 5
PHT.50 | 50 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #2 | ALSTOM | MICOM P545 | 33493423/11/15 | NUMERIK | 2019 |  | 0.118 | 84 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | Rev.02 NewSenayan-Senayan1,2 (1).pdf | 2019-11-14 |  | 0.12 | 84 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 5
PHT.51 | 51 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #1 | NR | PCS-931 | NRJB2015511480260 | NUMERIK | 2021 |  | 0.153 | 61 | 1 | 0.2 | 0 | - | - | [5 empty] | 151. LCD_PCS931_PCS9611_New Senayan - Senayan Baru II #1.pdf | 2020-11-13 |  | 0.153 | 61 | 1 | 0.2 | 1 | - | - | [6 empty] | 3.054
PHT.52 | 52 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #2 | ALSTOM | MICOM P545 | 34733776/03/19 | NUMERIK | 2021 |  | 0.301 | 61.699 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | REV01 152. LCD_P545_PCS9611_NEW SENAYAN - NEW SENAYAN II #2 (signed).pdf | 2021-04-01 |  | 0.3 | 62 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 3.05
PHT.53 | 53 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #1 | ALSTOM | MICOM P545 | 32288899/09/12 | NUMERIK | 2016 |  | 15.312 | 81.3 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | official tap setting proteksi sutt pik - daan mogot 1,2.pdf | 2019-07-31 |  | 15.31 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.6
PHT.54 | 54 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #2 | ALSTOM | MICOM P545 | 32288900/09/12 | NUMERIK | 2016 |  | 15.312 | 81.3 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | official tap setting proteksi sutt pik - daan mogot 1,2.pdf | 2019-07-31 |  | 15.31 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.6
PHT.55 | 55 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #1 | ALSTOM | MICOM P545 | 197931U | NUMERIK | 2016 |  | 15.645 | 81.338 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 2021 03 24 - Tap Setting GIS Pantai Indah Kapuk Bay Muarakarang Baru #1,2.pdf | 2021-03-24 |  | 15.82 | 81 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 4.93
PHT.56 | 56 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #2 | ALSTOM | MICOM P545 | 32197933/06/12 | NUMERIK | 2016 |  | 15.645 | 81.338 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 2021 03 24 - Tap Setting GIS Pantai Indah Kapuk Bay Muarakarang Baru #1,2.pdf | 2021-03-24 |  | 15.82 | 81 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 4.93
PHT.57 | 57 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV TOMANG | PHT 150kV GROGOL #1 | ALSTOM | MICOM P543 | 39652554/04/18 | NUMERIK | 2021 |  | 0.831 | 85 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | official tap setting LCD, DIST, OCR tomang - grogol 1,2.pdf | 2019-10-31 |  | 0.83 | 85 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 4.11
PHT.58 | 58 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV TOMANG | PHT 150kV GROGOL #2 | ALSTOM | MICOM P543 | 37055880/10/18 | NUMERIK | 2021 |  | 0.831 | 85 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | official tap setting LCD, DIST, OCR tomang - grogol 1,2.pdf | 2019-10-31 |  | 0.83 | 85 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 4.11
PHT.59 | 59 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #1 | NR | PCS-931 | NRJB20155116B0230[CE4B8B] | NUMERIK | 2021 |  | 0.153 | 61.699 | 1 | 0.2 | 1 | - | - | [5 empty] | 20210401_ULUJAMI_NEW SENAYAN_1 (LCD).pdf | 2021-04-03 |  | 0.153 | 62 | 1 | 0.2 | 1 | - | - | [6 empty] | 3.054
PHT.60 | 60 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #2 | GE | MICOM P545 | 34733777/03/19 | NUMERIK | 2021 |  | 0.301 | 61.699 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 20210401_ULUJAMI_NEW SENAYAN_2.pdf | 2021-04-03 |  | 0.3 | 62 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 3.05
PHT.61 | 61 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | ABB | RED670 | T2136184 | NUMERIK |  |  | 0 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | Rev00_LCD_DIST RED 670 GISTET MUARAKARANG BARU BAY DURIKOSAMBI main A - PASCA UJI LINE Z.pdf | 2024-10-15 |  | 0 | N/A | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.62 | 62 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | ABB | RED670 | T2136186 | NUMERIK |  |  | 0 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | Rev00_ LCD_DIST MKBRU - DURKOS _main B_siemens 7SL87_PASCA UJI LINE Z.pdf | 2024-10-15 |  | 0 | N/A | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.63 | 63 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | SIEMENS | 7SL87 | BM2110007783 | NUMERIK |  |  | 0.191 | 84.979 | 1 | 0.2 | 2 | - | - | [5 empty] | Rev00_LCD_DIST RED 670 GISTET MUARAKARANG BARU BAY DURIKOSAMBI main A - PASCA UJI LINE Z.pdf | 2024-10-15 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.64 | 64 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | SIEMENS | 7SL87 | BM2110006379 | NUMERIK |  |  | 0.191 | 84.979 | 1 | 0.2 | 2 | - | - | [5 empty] | Rev00_ LCD_DIST MKBRU - DURKOS _main B_siemens 7SL87_PASCA UJI LINE Z.pdf | 2024-10-15 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.65 | 65 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 |  | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | ABB | RED670 | T2136180 | NUMERIK |  |  | 0 | N/A |  | 0 | 0 | 0 | 0 | [8 empty] | 0 | N/A |  | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.66 | 66 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 |  | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | ABB | RED670 | T2136185 | NUMERIK |  |  | 0 | N/A |  | 0 | 0 | 0 | 0 | [8 empty] | 0 | N/A |  | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.67 | 67 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 |  | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | SIEMENS | 7SL87 | BM2110006364 | NUMERIK |  |  | 0 | 0 |  | 0 | 0 | - | - | [8 empty] | 0 | 0 |  | 0 | 0 | - | - | [6 empty] | 0
PHT.68 | 68 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 |  | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | SIEMENS | 7SL87 | BM2110006369 | NUMERIK |  |  | 0 | 0 |  | 0 | 0 | - | - | [8 empty] | 0 | 0 |  | 0 | 0 | - | - | [6 empty] | 0
PHT.69 | 69 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV CIKUPA #1 | ALSTOM | MICOM P545 | 34721258/02/19 | NUMERIK | 2019 |  | 2.261 | 80.731 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | 2021 01 22 - Tap Setting GI Curug Bay Cikupa #1.pdf | 2021-01-22 |  | 2.26 | 81 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 18.9
PHT.70 | 70 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#2 | #2 | 3200/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV CIKUPA #2 | ALSTOM | MICOM P545 | 34486826/06/18 | NUMERIK | 2019 |  | 5.698 | 84.806 | 1 | 0.3 | 2 | 30 | 150 | [8 empty] | 3.56 | 81 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 18.6
PHT.71 | 71 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 3200/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #1 | ALSTOM | MICOM P545 | 34486816/06/18 | NUMERIK | 2019 |  | 0.903 | 81 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | Curug-Summarecon.pdf | 2019-08-12 |  | 0.9 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.7
PHT.72 | 72 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #2 | ALSTOM | MICOM P545 | 34721255/02/19 | NUMERIK | 2019 |  | 0.565 | 81 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | Curug-Summarecon.pdf | 2019-08-12 |  | 0.57 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.7
PHT.73 | 73 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | #1 | 2000/1 | 150 kV/100 V | MPU | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | GE | L90 | AA2C17001630 | NUMERIK | 2018 |  | 0 | 82 | 1 | 0.2 | 1.5 | - | - | [5 empty] | (signed) Rev.01 L90 Gajah Tunggal - Pasar Kemis 1.pdf | 2021-08-25 |  | 0 | 82 | 1 | 0.3 | 0 | - | -
PHT.74 | 74 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | #1 | 2000/1 | 150 kV/100 V | MPU | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | ALSTOM | MICOM P543 | 32069228/02/12 | NUMERIK | 2021 |  | 1.85 | 82 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | (signed) Official Rev.02 Gajah Tunggal - Pasar Kemis Baru.pdf | 2021-08-10 |  | 1.85 | 82 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.6
PHT.75 | 75 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV TANGERANG BARU | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV ITS | PHT 150kV TANGERANG BARU | GE | MICOM P545 | 35301414/03/12 | NUMERIK | 2021 |  | 4.201 | 87.3 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 132. [signed] KTT ITS Bay Tangerang Baru.pdf | 2021-07-29 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.76 | 76 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV CENGKARENG BARU | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV ITS | PHT 150kV CENGKARENG BARU | AREVA | MICOM P543 | 3379380/04/09 | NUMERIK | 2021 |  | 6.881 | 87.3 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 133. [signed] KTT ITS Bay Cengkareng Baru.pdf | 2021-07-29 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.77 | 77 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV KONSUMEN | #1 | 300/1 | 150 kV/100 V | MPU | GI 150KV ITS | PHT 150kV KONSUMEN | SIEMENS | 7SL87 | BM2102005251 | NUMERIK | 2021 |  | 0 | 62.709 | 1 | 0.2 | 2 | - | - | [5 empty] | 135. [signed] GI ITS Bay Consumer.pdf | 2021-07-29 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.78 | 78 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#1 | #1 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV CIKUPA #1 | ALSTOM | MICOM P442 | 31830604/07/11 | NUMERIK |  |  | 0 | 0 | 5 | N/A | N/A | - | - | [8 empty] | 0 | 0 | 5 | N/A | N/A | - | - | [6 empty] | 0
PHT.79 | 79 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#2 | #2 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV CIKUPA #2 | ALSTOM | MICOM P442 | 31830599/07/11 | NUMERIK |  |  | 0 | 0 | 5 | N/A | N/A | - | - | [8 empty] | 0 | 0 | 5 | N/A | N/A | - | - | [6 empty] | 0
PHT.80 | 80 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#1 | #1 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV JATAKE BARU #1 | NR | PCS-931 | NRJB20155119B0540 | NUMERIK | 2021 |  | 0.211 | 82.15 | 5 | 1 | 1 | - | - | [5 empty] | GI Jatake Lama bay Jatake II 1,2_PCS931 Revisi Final (1).pdf | 2021-02-01 |  | 0.234 | 82 | 5 | 1 | 0 | - | - | [6 empty] | 3.12
PHT.81 | 81 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#2 | #2 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV JATAKE BARU #2 | NR | PCS-931 | NRJB20155119B0550 | NUMERIK | 2021 |  | 0.211 | 82.15 | 5 | 1 | 1 | - | - | [5 empty] | GI Jatake Lama bay Jatake II 1,2_PCS931 Revisi Final (1).pdf | 2021-02-01 |  | 0.234 | 82 | 5 | 1 | 0 | - | - | [6 empty] | 3.12
PHT.82 | 82 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | NR | PCS-931 | NRJB2015511830010 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.224 | 1 | - | - | [5 empty] | Jatake-Maxi (1).pdf | 2018-08-30 |  | 0.075 | 86 | 1 | 0.2 | 1 | - | - | [6 empty] | 0.99
PHT.83 | 83 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | NR | PCS-931 | NRJB2015511830040 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.224 | 1 | - | - | [5 empty] | Jatake-Maxi (1).pdf | 2018-08-30 |  | 0.08 | 73 | 1 | 0.2 | 1 | - | - | [6 empty] | 1.1
PHT.84 | 84 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | NR | PCS-931 | NRJB2015511830020 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.224 | 1 | - | - | [5 empty] | Jatake-Maxi (1).pdf | 2018-08-30 |  | 0.075 | 86 | 1 | 0.2 | 1 | - | - | [6 empty] | 0.99
PHT.85 | 85 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | NR | PCS-931 | NRJB2015511830030 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.224 | 1 | - | - | [5 empty] | Jatake-Maxi (1).pdf | 2018-08-30 |  | 0.08 | 73 | 1 | 0.2 | 1 | - | - | [6 empty] | 1.1
PHT.86 | 86 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | NR | PCS-931 | NRJB2015511830070 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.2 | 0 | - | - | [5 empty] | Maxi-Jatake (1).pdf | 2018-08-30 |  | 0.075 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 0.99
PHT.87 | 87 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | NR | PCS-931 | NRJB2015511830100 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.2 | 0 | - | - | [5 empty] | Maxi-Jatake (1).pdf | 2018-08-31 |  | 0.075 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 0.99
PHT.88 | 88 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | NR | PCS-931 | NRJB2015511830080 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.2 | 0 | - | - | [5 empty] | Maxi-Jatake (1).pdf | 2018-09-01 |  | 0.075 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 0.99
PHT.89 | 89 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | NR | PCS-931 | NRJB2015511830090 | NUMERIK | 2019 |  | 0.075 | 83.256 | 1 | 0.2 | 0 | - | - | [5 empty] | Maxi-Jatake (1).pdf | 2018-09-02 |  | 0.075 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 0.99
PHT.90 | 90 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #1 | NR | PCS-931 | NRJB2029221960030 | NUMERIK | 2021 |  | 3.339 | 82.275 | 1 | 0.2 | 1 | - | - | [5 empty] | PCS931_TBII-Balaraja.pdf | 2020-05-13 |  | 3.339 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 7.69
PHT.91 | 91 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #2 | NR | PCS-931 | NRJB2029221960100 | NUMERIK | 2021 |  | 3.339 | 82.275 | 1 | 0.2 | 1 | - | - | [5 empty] | PCS931_TBII-Balaraja.pdf | 2020-05-13 |  | 3.339 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 7.69
PHT.92 | 92 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #1 | NR | PCS-931 | NRJB2006301870170 | NUMERIK | 2021 |  | 9.36 | 82.24 | 1 | 0 | 0 | - | - | [5 empty] | tap setting DIST_OCR_PCS931_PCS9611_OHL Tangerang Baru II - Lontar 1,2_rev02 (AR by Selector Switch).pdf | 2020-11-07 |  | 9.36 | 82 | 1 | 0 | 0 | - | - | [6 empty] | 12.58
PHT.93 | 93 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #2 | NR | PCS-931 | NRJB2015511680190[A74B17] | NUMERIK | 2021 |  | 9.36 | 82.24 | 1 | 0 | 0 | - | - | [5 empty] | tap setting DIST_OCR_PCS931_PCS9611_OHL Tangerang Baru II - Lontar 1,2_rev02 (AR by Selector Switch).pdf | 2020-11-07 |  | 9.36 | 82 | 1 | 0 | 0 | - | - | [6 empty] | 12.58
PHT.94 | 94 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #1 | NR | PCS-931 | NRJB2029221960020 | NUMERIK | 2021 |  | 1.98 | 82.725 | 1 | 0.2 | 1 | - | - | [5 empty] | PCS931_TBII-Suvarna.pdf | 2020-05-13 |  | 1.98 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 4.56
PHT.95 | 95 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #2 | NR | PCS-931 | NRJB2029221960010 | NUMERIK | 2021 |  | 1.98 | 82.725 | 1 | 0.2 | 1 | - | - | [5 empty] | PCS931_TBII-Suvarna.pdf | 2020-05-13 |  | 1.98 | 83 | 1 | 0.2 | 1 | - | - | [6 empty] | 4.56
PHT.96 | 96 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #1 | GE | MICOM P546 | 36265528/12/22 | NUMERIK | 2021 |  | 11.284 | 76.22 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | LCD_DIST UGC Tangerang Baru - GIS Lontar_GE P546_r_230520_090703.pdf | 2023-05-19 |  | 11.28 | 76 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 21.22
PHT.97 | 97 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #2 | GE | MICOM P546 | 36265524/12/22 | NUMERIK | 2021 |  | 11.284 | 76.22 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | LCD_DIST UGC Tangerang Baru - GIS Lontar_GE P546_r_230520_090703.pdf | 2023-05-19 |  | 11.28 | 76 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 21.28
PHT.98 | 98 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV ITS | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV ITS | GE | MICOM P545 | 35298236/03/21 | NUMERIK | 2021 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [5 empty] | 136.[signed] TANGERANG BARU BAY KTT ITS.pdf | 2021-07-29 |  | 3.15 | 87 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 2.45
PHT.99 | 99 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | AREVA | MICOM P543 | 3379379/05/09 | NUMERIK | 2021 |  | 10.804 | 87.293 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | GI Tangerang Baru Bay Cengkareng (1).pdf | 2017-09-12 |  | 8.25 | 87 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.5
PHT.100 | 100 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV DADAP #1 | AREVA | MICOM P546 | 34434876/05/18 | NUMERIK |  |  | 3.487 | 82.725 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 20200219_Tap Setting Teluk Naga - Dadap 1&2.pdf | 2020-02-19 |  | 3.49 | 83 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.13
PHT.101 | 101 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV DADAP #2 | AREVA | MICOM P546 | 34450419/05/18 | NUMERIK |  |  | 3.487 | 82.725 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | 20200219_Tap Setting Teluk Naga - Dadap 1&2.pdf | 2020-02-19 |  | 3.49 | 83 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.13
PHT.102 | 102 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#1 | #1 | 1600/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #1 | GE | MICOM P546 |  | NUMERIK | 2018 |  | 2.77 | 82.15 | 1 | 0.2 | 2 | 30 | 80 | [5 empty] | P443 OHL Teluknaga-Sepatan.pdf | 2018-03-06 |  | 2.77 | 82.15 | 1 | 0.2 | 2 | 30 | 80 | [6 empty] | 9.17
PHT.103 | 103 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#2 | #2 | 1600/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #2 | GE | MICOM P546 |  | NUMERIK | 2018 |  | 2.77 | 82.15 | 1 | 0.2 | 2 | 30 | 80 | [5 empty] | P443 OHL Teluknaga-Sepatan.pdf | 2018-03-06 |  | 2.77 | 82.15 | 1 | 0.2 | 2 | 30 | 80 | [6 empty] | 9.17
PHT.104 | 104 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #1 | NR | PCS-931 | NRJB20155119B0340 | NUMERIK | 2021 |  | 1.321 | 82.15 | 1 | 0.2 | 1 | - | - | [5 empty] | GI Jatake II bay Jatake Lama ,12_PCS931 Revisi Final (1).pdf | 2021-02-01 |  | 1.168 | 82 | 1 | 0.2 | 0 | - | - | [6 empty] | 3.12
PHT.105 | 105 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #2 | NR | PCS-931 | NRJB20155119B0050 | NUMERIK | 2021 |  | 1.321 | 82.15 | 1 | 0.2 | 1 | - | - | [5 empty] | GI Jatake II bay Jatake Lama ,12_PCS931 Revisi Final (1).pdf | 2021-02-01 |  | 1.168 | 82 | 1 | 0.2 | 0 | - | - | [6 empty] | 3.12
PHT.106 | 106 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #1 | NR | PCS-931 | NRJB20155119B0370 | NUMERIK | 2021 |  | 2.571 | 82.15 | 1 | 0.2 | 1 | - | - | [5 empty] | GI Jatake II bay Tangerang Lama ,12_PCS931 Revisi Final.pdf | 2021-02-01 |  | 2.571 | 82 | 1 | 0.2 | 1 | - | - | [6 empty] | 6.87
PHT.107 | 107 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #2 | NR | PCS-931 | NRJB20155119B0360 | NUMERIK | 2021 |  | 2.571 | 82.15 | 1 | 0.2 | 1 | - | - | [5 empty] | GI Jatake II bay Tangerang Lama ,12_PCS931 Revisi Final.pdf | 2021-02-01 |  | 2.571 | 82 | 1 | 0.2 | 1 | - | - | [6 empty] | 6.87
PHT.108 | 108 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #1 | SCHNEIDER | MICOM P443 | 39615255/07/17 | NUMERIK | 2021 |  | 9.446 | 82.2 | 1 | N/A | N/A | - | - | [5 empty] | official tap setting DIST_OCR_schneider p443_p142_OHL Lontar - Tangerang Baru II 1,2_rev01.pdf | 2020-06-20 |  | 9.446 | 82.2 | 1 | N/A | N/A | - | - | [6 empty] | 12.58
PHT.109 | 109 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #2 | SCHNEIDER | MICOM P443 | 39619256/07/17 | NUMERIK | 2021 |  | 9.446 | 82.2 | 1 | N/A | N/A | - | - | [5 empty] | official tap setting DIST_OCR_schneider p443_p142_OHL Lontar - Tangerang Baru II 1,2_rev01.pdf | 2020-06-20 |  | 9.446 | 82.2 | 1 | N/A | N/A | - | - | [6 empty] | 12.58
PHT.110 | 110 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV DADAP #1 | ALSTOM | MICOM P446 | 34389472/03/18 | NUMERIK |  |  | 14.549 | 82.725 | 1 | N/A | N/A | - | - | [5 empty] | 20200220_LONTAR-DADAP 1_2.pdf | 2020-02-20 |  | 14.94 | 83 | 1 | N/A | N/A | - | - | [6 empty] | 26.26
PHT.111 | 111 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV DADAP #2 | ALSTOM | MICOM P446 | 34486172/06/18 | NUMERIK |  |  | 14.549 | 82.725 | 1 | N/A | N/A | - | - | [5 empty] | 20200220_LONTAR-DADAP 1_2.pdf | 2020-02-20 |  | 14.94 | 83 | 1 | N/A | N/A | - | - | [6 empty] | 26.26
PHT.112 | 112 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #1 | GE | MICOM P546 | 36265529/12/22 | NUMERIK |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.113 | 113 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #2 | GE | MICOM P546 | 36265525/12/22 | NUMERIK |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.114 | 114 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #1 | GE | MICOM P545 | 36039278/03/22 | NUMERIK |  |  | 1.272 | 84.339 | 5 | 10.2 | 102 | 30 | 150 | [5 empty] | 70. LCD_545_CENGKARENG BAY DURIKOSAMBI 1^J2.pdf | 2022-12-04 |  | 1.272 | 84 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 10.32
PHT.115 | 115 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #2 | GE | MICOM P545 | 36039283/03/22 | NUMERIK |  |  | 1.272 | 84.339 | 5 | 0.21 | 210 | 30 | 150 | [5 empty] | 70. LCD_545_CENGKARENG BAY DURIKOSAMBI 1^J2.pdf | 2022-12-04 |  | 1.272 | 84 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 10.32
PHT.116 | 116 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #1 | AREVA | MICOM P545 | 3379381/07/10 | NUMERIK | 2012 |  | 0.05 | 88.797 | 5 | 10.2 | 102 | 30 | 150 | [5 empty] | Tap Setting GI Cengkareng Lama.pdf | 2017-12-06 |  | 0.66 | 89 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 0.4
PHT.117 | 117 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#2 | #2 | 3000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #2 | AREVA | MICOM P545 | 3379382/05/09 | NUMERIK | 2011 |  | 0.05 | 88.797 | 5 | 10.2 | 102 | 30 | 150 | [5 empty] | 2022 05 12 - Tap Setting GI Cengkareng - Cengkareng Baru #2.pdf | 2022-05-12 |  | 0.124 | 89 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 0.4
PHT.118 | 118 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV TANGERANG #1 | SIEMENS | 7SL87 | BM1911005993 | NUMERIK | 2021 |  | 0.06 | 82 | 5 | 0.2 | 2 | - | - | [5 empty] | Rev01.GRZ100 CNKNG bay TGRNG 1,2 - 30 08 2019.pdf | 2019-08-30 |  | 0.06 | 82 | 5 | 1 | 10 | - | - | [6 empty] | 9.23
PHT.119 | 119 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV TANGERANG #2 | SIEMENS | 7SL87 | BM1911005990 | NUMERIK | 2021 |  | 0.06 | 82 | 5 | 0.2 | 2 | - | - | [5 empty] | Rev01.GRZ100 CNKNG bay TGRNG 1,2 - 30 08 2019.pdf | 2019-08-30 |  | 0.06 | 82 | 5 | 1 | 10 | - | - | [6 empty] | 9.23
PHT.120 | 120 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#1 | #1 | 1000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #1 | Siemens | 7SL87 |  | NUMERIK | 2019 |  | 0 | 0 | 1 | 0.2 | 2 | - | - | [5 empty] | CKRNG-BASUTA.pdf | 2019-02-14 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.121 | 121 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#2 | #2 | 1000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #2 | Siemens | 7SL87 |  | NUMERIK | 2019 |  | 0 | 0 | 1 | 0.2 | 2 | - | - | [5 empty] | CKRNG-BASUTA.pdf | 2019-02-14 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.122 | 122 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #1 | ALSTOM | MICOM P545 | 33980376/02/17 | NUMERIK | 2018 |  | 0.33 | 88.797 | 1 | 1 | 10 | 30 | 150 | [5 empty] | 2022 05 11 - Tap Setting GI Cengkareng Baru - Cengkareng #1,2.pdf | 2022-05-12 |  | 0.12 | 89 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 0.4
PHT.123 | 123 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #2 | ALSTOM | MICOM P545 | 33980375/02/17 | NUMERIK | 2018 |  | 0.33 | 88.797 | 1 | 1 | 10 | 30 | 150 | [5 empty] | 2022 05 11 - Tap Setting GI Cengkareng Baru - Cengkareng #1,2.pdf | 2022-05-12 |  | 0.12 | 89 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 0.4
PHT.124 | 124 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV ITS | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV ITS | ALSTOM | MICOM P545 | 33980378/02/17 | NUMERIK | 2018 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 6.88 | 87 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.13
PHT.125 | 125 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU | ALSTOM | MICOM P545 | 33980371/02/17 | NUMERIK | 2018 |  | 2.161 | 87.293 | 1 | 1 | 10 | 30 | 150 | [5 empty] | 20171206_CENGKARENG BARU_TANGERANG BARU_1&2.pdf | 2017-12-06 |  | 11 | 87 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 6.5
PHT.126 | 126 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #1 | ALSTOM | MICOM P543 | 32069227/02/12 | NUMERIK | 2015 |  | 0.417 | 76.971 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | 2021 03 23 - Tap Setting GI Ciledug Bay Alam Sutera #1 - Rev02.pdf | 2021-03-23 |  | 0.42 | 77 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 3.25
PHT.127 | 127 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #2 | ALSTOM | MICOM P545 | 34665003/12/18 | NUMERIK | 2020 |  | 0.278 | 76.971 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | 2021 03 23 - Tap Setting GI Ciledug Bay Alam Sutera #2 - Rev01.pdf | 2021-03-23 |  | 0.44 | 81 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 3.7
PHT.128 | 128 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#1 | #1 | 3200/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV METLAND #1 | ALSTOM | MICOM P545 | 34486736/06/18 | NUMERIK | 2019 |  | 6.905 | 77.091 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | tap setting UGC Ciledug - Kembangan II 1_LCD DIST-P545_OCR-P142.pdf | 2022-03-03 |  | 6.91 | 77 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 5.36
PHT.129 | 129 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV METLAND #2 | ALSTOM | MICOM P545 | 34721257/02/19 | NUMERIK | 2019 |  | 4.315 | 77.091 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | tap setting UGC Ciledug - Kembangan II 2_LCD DIST-P545_OCR-P142.pdf | 2022-03-03 |  | 4.32 | 77 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 5.356
PHT.130 | 130 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #1 | GE | MICOM P545 | 36039279/03/22 | NUMERIK |  |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [8 empty] | 1.272 | 84 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 10.32
PHT.131 | 131 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #2 | GE | MICOM P545 | 36039282/03/22 | NUMERIK |  |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [8 empty] | 1.272 | 84 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 10.32
PHT.132 | 132 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV LMK | #1 | 1000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV LMK | ALSTOM | MICOM P443 | 34486778/06/18 | NUMERIK | 2019 |  | 0.02 | 80.54 | 5 | N/A | N/A | - | - | [8 empty] | 0.02 | 80.54 | 5 | N/A | N/A | - | - | [6 empty] | 0.3
PHT.133 | 133 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#1 | #1 | 1600/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #1 | SIEMENS | 7SL87 | BM1809009344 | NUMERIK | 2019 |  | 0 | 0 | 5 | 0 | 0 | - | - | [8 empty] | 0.06 | 82 | 5 | 1.25 | 12.5 | - | - | [6 empty] | 6.47
PHT.134 | 134 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#2 | #2 | 1600/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #2 | SIEMENS | 7SL87 | BM1909000272 | NUMERIK | 2020 |  | 0 | 0 | 5 | 0 | 0 | - | - | [8 empty] | 0.06 | 82 | 5 | 1.25 | 12.5 | - | - | [6 empty] | 6.47
PHT.135 | 135 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #1 | ALSTOM | MICOM P545 | 34483353/06/18 | NUMERIK | 2019 |  | 0.624 | 72 | 5 | 1 | 10 | 30 | 150 | [5 empty] | Official Durikosambi-KebunJeruk.pdf | 2019-08-12 |  | 0.624 | 72 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 10.2
PHT.136 | 136 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #2 | ALSTOM | MICOM P545 | 34482260/06/18 | NUMERIK | 2019 |  | 0.31 | 73.74 | 5 | 1 | 4.6 | 30 | 80 | [5 empty] | DAFTAR SETELAN RELAI PROTEKSI Gl 150kV DURIKOSAMBI_07.04.26.pdf | 2026-04-07 |  | 0.31 | 73.74 | 5 | 1.5 | 10 | 30 | 150 | [6 empty] | 10.2
PHT.137 | 137 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #1 | ALSTOM | MICOM P545 | 33081355/10/14 | NUMERIK | 2018 |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [8 empty] | 0.574 | 73 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 6.84
PHT.138 | 138 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #2 | ALSTOM | MICOM P546 | 33081360/10/14 | NUMERIK | 2018 |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 | [8 empty] | 0.574 | 73 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 6.84
PHT.139 | 139 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#1 | #1 | 3000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #1 | ABB | RED670 | T1645095 | NUMERIK | 2020 |  | 2.591 | N/A | 5 | 0.2 | 1 | 30 | 80 | [5 empty] | official tap setting proteksi sutt durikosambi - daan mogot 1_rev01.pdf | 2019-08-28 |  | 2.591 | N/A | 5 | 0.2 | 1 | 0 | 0 | [6 empty] | 2.1
PHT.140 | 140 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #2 | ABB | RED670 | T1645094 | NUMERIK | 2020 |  | 2.591 | N/A | 5 | 0.2 | 1 | 30 | 80 | [5 empty] | official tap setting proteksi sutt durikosambi - daan mogot 2_rev01.pdf | 2019-08-28 |  | 2.591 | N/A | 5 | 0.2 | 1 | 0 | 0 | [6 empty] | 2.1
PHT.141 | 141 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV CENGKARENG #1 | SIEMENS | 7SL87 | BM1911005996 | NUMERIK | 2021 |  | 0.06 | 82 | 5 | 1 | 10 | - | - | [5 empty] | 2020 01 31 - Tap Setting GI Tangerang Lama bay Cengkareng 1,2.pdf | 2020-02-03 |  | 0.06 | 82 | 5 | 1 | 10 | - | - | [6 empty] | 9.23
PHT.142 | 142 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV CENGKARENG #2 | SIEMENS | 7SL87 | BM1911005987 | NUMERIK | 2021 |  | 0.06 | 82 | 5 | 1 | 10 | - | - | [5 empty] | 2020 01 31 - Tap Setting GI Tangerang Lama bay Cengkareng 1,2.pdf | 2020-02-03 |  | 0.06 | 82 | 5 | 1 | 10 | - | - | [6 empty] | 9.23
PHT.143 | 143 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #1 | NR | PCS-931 | NRJB20155119B0560 | NUMERIK | 2021 |  | 0.514 | 82.15 | 5 | 1 | 1 | - | - | [5 empty] | GI Tangerang Lama bay Jatake II-1,2 PCS931 Revisi Final.pdf | 2021-02-01 |  | 0.514 | 82 | 5 | 1 | 1 | - | - | [6 empty] | 6.87
PHT.144 | 144 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #2 | NR | PCS-931 | NRJB20155119B0570 | NUMERIK | 2021 |  | 0.514 | 82.15 | 5 | 1 | 1 | - | - | [5 empty] | GI Tangerang Lama bay Jatake II-1,2 PCS931 Revisi Final.pdf | 2021-02-01 |  | 0.514 | 82 | 5 | 1 | 1 | - | - | [6 empty] | 6.87
PHT.145 | 145 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #1 | ALSTOM | MICOM P543 | 32069229/02/12 | NUMERIK | 2014 |  | 0.278 | 76.971 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | GI Alam Sutera Bay Ciledug.pdf | 2019-02-01 |  | 0.56 | 77 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 3.25
PHT.146 | 146 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #2 | ALSTOM | MICOM P545 | 34486819/06/18 | NUMERIK | 2020 |  | 0.278 | 76.971 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | GI Alam Sutera Bay Ciledug.pdf | 2019-02-01 |  | 0.44 | 81 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 3.7
PHT.147 | 147 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #1 | ABB | RED670 | T1809136 | NUMERIK | 2019 |  | 0 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | Official Alsut-Sumarecon.pdf | 2019-05-09 |  | 1.093 | N/A | 1 | 0.2 | 0 | 30 | 80 | [6 empty] | 7.2
PHT.148 | 148 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #2 | ABB | RED670 | T1809137 | NUMERIK | 2019 |  | 0 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | Official Alsut-Sumarecon.pdf | 2019-05-09 |  | 1.093 | N/A | 1 | 0.2 | 0 | 30 | 80 | [6 empty] | 7.2
PHT.149 | 149 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#1 | #1 | 3200/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV METLAND #1 | SIEMENS | 7SL87 | BM1802009731 | NUMERIK | 2019 |  | 0.122 | 23.661 | 5 | 0.2 | 2 | - | - | [5 empty] | tap setting UGC Kembangan - Kembangan II _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-03-04 |  | 0 | 0 | 5 | 0 | 0 | - | - | [6 empty] | 0
PHT.150 | 150 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#2 | #2 | 3200/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV METLAND #2 | SIEMENS | 7SL87 | BM1801000462 | NUMERIK | 2019 |  | 0.122 | 23.661 | 5 | 0.2 | 2 | - | - | [5 empty] | tap setting UGC Kembangan - Kembangan II _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-03-04 |  | 0 | 0 | 5 | 0 | 0 | - | - | [6 empty] | 0
PHT.151 | 151 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #1 | ALSTOM | MICOM P545 | 33081356/10/14 | NUMERIK | 2018 |  | 0.105 | 72.875 | 5 | 0.3 | 2 | 30 | 150 | [5 empty] | 2021 01 22 - Tap Setting GIS Kembangan Bay Durikosambi #1,2.pdf | 2021-01-22 |  | 0.574 | 73 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 6.84
PHT.152 | 152 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #2 | ALSTOM | MICOM P546 | 33081359/10/14 | NUMERIK | 2018 |  | 0.105 | 72.875 | 5 | 0.3 | 2 | 30 | 150 | [5 empty] | 2021 01 22 - Tap Setting GIS Kembangan Bay Durikosambi #1,2.pdf | 2021-01-22 |  | 0.574 | 73 | 5 | 1 | 10 | 30 | 150 | [6 empty] | 6.84
PHT.153 | 153 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #1 | GE | MICOM P546 |  | NUMERIK | 2025 |  | 0.15 | 72.87 | 5 | 0.93 | 9.25 | 30 | 80 | [5 empty] | (Official) KEMBANGAN - NEW SENAYAN 1 DAN 2 - TAP MICOM P545-546.pdf | 2025-11-06 |  | 0 | 0 | 5 | 0.2 | 2 | 30 | 150 | [6 empty] | 0
PHT.154 | 154 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #2 | GE | MICOM P546 |  | NUMERIK | 2025 |  | 0.15 | 72.87 | 5 | 0.93 | 9.25 | 30 | 80 | [5 empty] | (Official) KEMBANGAN - NEW SENAYAN 1 DAN 2 - TAP MICOM P545-546.pdf | 2025-11-06 |  | 0 | 0 | 5 | 0.2 | 2 | 30 | 150 | [6 empty] | 0
PHT.155 | 155 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #1 | NR | PCS-931 |  | NUMERIK | 2019 |  | 0.585 | 80.966 | 5 | 1 | 0 | - | - | [5 empty] | GIS KEMBANGAN BAY PETUKANGAN 1 (OK).pdf | 2025-06-20 |  | 0.585 | 80.966 | 5 | 1 | 0 | - | - | [6 empty] | 9.52
PHT.156 | 156 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #2 | NR | PCS-931 |  | NUMERIK | 2019 |  | 0.585 | 80.966 | 5 | 1 | 0 | - | - | [5 empty] | GIS KEMBANGAN BAY PETUKANGAN 1 (OK).pdf | 2025-06-20 |  | 0.585 | 80.966 | 5 | 1 | 0 | - | - | [6 empty] | 9.52
PHT.157 | 157 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV KEMBANGAN #1 | SIEMENS | 7SL87 | BM1802009734 | NUMERIK | 2022 |  | 0.383 | 23.661 | 1 | 0.2 | 2 | - | - | [5 empty] | tap setting UGC Kembangan II - Kembangan _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-02-09 |  | 0.383 | 23.66 | 1 | 0.2 | 2 | - | - | [6 empty] | 2.61
PHT.158 | 158 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV KEMBANGAN #2 | SIEMENS | 7SL87 | BM1801000459 | NUMERIK | 2022 |  | 0.383 | 23.661 | 1 | 0.2 | 2 | - | - | [5 empty] | tap setting UGC Kembangan II - Kembangan _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-02-09 |  | 0.383 | 23.66 | 1 | 0.2 | 2 | - | - | [6 empty] | 2.61
PHT.159 | 159 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV CILEDUG #1 | ALSTOM | MICOM P545 | 34486820/06/18 | NUMERIK | 2022 |  | 4.315 | 77.091 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | TAPSET~3.PDF | 2023-10-19 |  | 4.32 | 77 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 5.36
PHT.160 | 160 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV CILEDUG #2 | ALSTOM | MICOM P545 | 34486817 | NUMERIK | 2022 |  | 4.315 | 77.091 | 1 | 0.3 | 2 | 30 | 150 | [5 empty] | TAPSET~3.PDF | 2023-10-19 |  | 4.32 | 77 | 1 | 0.3 | 2 | 30 | 150 | [6 empty] | 5.36
PHT.161 | 161 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #1 | ABB | RED670 | T1809138 | NUMERIK | 2019 |  | 1.093 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | 20190506_SUMMARECON_ALAM SUTERA_1&2.pdf | 2019-05-09 |  | 1.093 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [6 empty] | 7.2
PHT.162 | 162 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #2 | ABB | RED670 | T1809135 | NUMERIK | 2019 |  | 1.093 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | 20190506_SUMMARECON_ALAM SUTERA_1&2.pdf | 2019-05-09 |  | 1.093 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [6 empty] | 7.2
PHT.163 | 163 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #1 | ALSTOM | MICOM P545 | 34486822/06/18 | NUMERIK | 2019 |  | 0.565 | 81 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | Summarecon-Curug.pdf | 2019-08-12 |  | 0.57 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.7
PHT.164 | 164 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #2 | ALSTOM | MICOM P545 | 34486818/06/18 | NUMERIK | 2019 |  | 0.565 | 81 | 1 | 0.2 | 2 | 30 | 150 | [5 empty] | Summarecon-Curug.pdf | 2019-08-12 |  | 0.57 | 81 | 1 | 0.2 | 2 | 30 | 150 | [6 empty] | 4.7
PHT.165 | 165 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | TOSHIBA | GRL 200 | VNT0682FM0001-1 | NUMERIK | 2020 |  | 7.649 | 85 | 1 | 0.18 | 1.8 | 30 | 80 | [5 empty] | NR PCS931 DURKOS-GANDUL.pdf | 2019-10-16 |  | 7.64 | 23 | 1 | 0.18 | 1.8 | 30 | 80 | [6 empty] | 0
PHT.166 | 166 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | TOSHIBA | GRL 200 | VNT0682FM0001-2 | NUMERIK | 2020 |  | 0.878 | 86 | 1 | 0.225 | 3 | 30 | 80 | [5 empty] | Rev 01GISTET Durikosambi Bay Kembangan 1-2 Main-2.pdf | 2019-10-09 |  | 0.93 | 86 | 1 | 0.22 | 3 | 30 | 80 | [6 empty] | 0
PHT.167 | 167 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | ABB | RED670 | T2136181 | NUMERIK |  |  | 2.674 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | Copy of Rev00_LCD_DIST GISTET Durikosambi bay Muarakarang Baru 1,2_Main A dan B - PASCA UJI LINE Z (1).pdf | 2019-10-15 |  | 0 | N/A | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.168 | 168 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | ABB | RED670 | T2136163 | NUMERIK |  |  | 2.674 | N/A | 1 | 0.2 | 0.8 | 30 | 80 | [5 empty] | Copy of Rev00_LCD_DIST GISTET Durikosambi bay Muarakarang Baru 1,2_Main A dan B - PASCA UJI LINE Z (1).pdf | 2019-10-15 |  | 0 | N/A | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.169 | 169 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | NR | PCS-931 | NRJB20155116B0350 | NUMERIK | 2020 |  | 7.649 | 85 | 1 | 0 | 0 | - | - | [5 empty] | TOSHIBA GRL 200 DURKOS-GANDUL.pdf | 2019-10-16 |  | 7.649 | 85 | 1 | 0 | 0.04 | - | - | [6 empty] | 34.093
PHT.170 | 170 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | SIEMENS | 7SL87 | BM1801010766 | NUMERIK | 2020 |  | 0.2777 | 86 | 1 | 0.2 | 2 | - | - | [5 empty] | Rev 01 GISTET Durikosambi Bay Kembangan 1-2 Main-1.pdf | 2019-10-09 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.171 | 171 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | SIEMENS | 7SL87 | BM2110007778 | NUMERIK |  |  | 0.191 | 84.979 | 1 | 0.2 | 2 | - | - | [5 empty] | Copy of Rev00_LCD_DIST GISTET Durikosambi bay Muarakarang Baru 1,2_Main A dan B - PASCA UJI LINE Z (1).pdf | 2019-10-15 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.172 | 172 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | SIEMENS | 7SL87 | BM2110007773 | NUMERIK |  |  | 0.191 | 84.979 | 1 | 0.2 | 2 | - | - | [5 empty] | Copy of Rev00_LCD_DIST GISTET Durikosambi bay Muarakarang Baru 1,2_Main A dan B - PASCA UJI LINE Z (1).pdf | 2019-10-15 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.173 | 173 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | TOSHIBA | GRL 200 | VNT0605FM0001-1 | NUMERIK |  |  | 0.866 | 85.258 | 1 | 0.248 | 1.654 | 30 | 80 | [5 empty] | LCD_DIST GITET KMBGAN - DURKOS 1,2 _main A_Toshiba GRL200_rev00.pdf | 2025-06-28 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.174 | 174 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | TOSHIBA | GRL 200 | VNT0605FM0001-2 | NUMERIK | 2020 |  | 0.866 | 85.258 | 1 | 0.248 | 1.654 | 30 | 80 | [5 empty] | LCD_DIST GITET KMBGAN - DURKOS 1,2 _main A_Toshiba GRL200_rev00.pdf | 2025-06-28 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 0
PHT.175 | 175 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | SIEMENS | 7SL87 | BM1801010778 | NUMERIK | 2022 |  | 0.2777 | 86 | 1 | 0.2 | 2 | - | - | [5 empty] | Copy of official tap setting LCD_DIST GISTET kembangan - balaraja_main A_siemens 7SL87_AR 7VK86.pdf | 2021-05-25 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.176 | 176 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | SIEMENS | 7SL87 | BM1801010762 | NUMERIK | 2022 |  | 0.2777 | 86 | 1 | 0.2 | 2 | - | - | [5 empty] | Copy of official tap setting LCD_DIST GISTET kembangan - balaraja_main A_siemens 7SL87_AR 7VK86.pdf | 2021-05-25 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.177 | 177 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 2000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | TOSHIBA | GRL 200 | VNT0773FM0001-1 | NUMERIK | 2019 |  | 3.3856 | 84.892 | 1 | 0.73 | 3.6 | 30 | 80 | [5 empty] | Toshiba GITET Kembangan Bay Gandul.pdf | 2018-12-01 |  | 8.46 | 84 | 1 | 0.73 | 3.6 | 30 | 80 | [6 empty] | 0
PHT.178 | 178 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 2000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | TOSHIBA | GRL 200 | VNT0773FM0001-2 | NUMERIK | 2019 |  | 3.3856 | 84.892 | 1 | 0.73 | 3.6 | 30 | 80 | [5 empty] | Toshiba GITET Kembangan Bay Gandul.pdf | 2018-12-01 |  | 8.46 | 84 | 1 | 0.73 | 3.6 | 30 | 80 | [6 empty] | 0
PHT.179 | 179 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | SIEMENS | 7SL87 | BM1801010448 | NUMERIK |  |  | 0.222 | 85.258 | 1 | 0.2 | 2 | - | - | [5 empty] | LCD_DIST GITET KMBGAN - DURKOS 1,2 _main.pdf | 2025-06-28 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.180 | 180 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | SIEMENS | 7SL87 | BM1801010453 | NUMERIK | 2020 |  | 0.222 | 85.258 | 1 | 0.2 | 2 | - | - | [5 empty] | LCD_DIST GITET KMBGAN - DURKOS 1,2 _main.pdf | 2025-06-28 |  | 0 | 0 | 1 | 0 | 0 | - | - | [6 empty] | 0
PHT.181 | 181 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | TOSHIBA | GRL 200 | VNT0682 FM 001-3 | NUMERIK | 2022 |  | 8.41 | 86 | 1 | 0.3 | 3 | 30 | 80 | [5 empty] | Copy of official tap setting GISTET KEMBANGAN BAY BALARAJA main B_toshiba GRL200.pdf | 2021-05-21 |  | 9.92 | 86 | 1 | 0.3 | 3 | 30 | 80 | [6 empty] | 0
PHT.182 | 182 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | TOSHIBA | GRL 200 | VNT0682 FM 001-6 | NUMERIK | 2022 |  | 8.41 | 86 | 1 | 0.3 | 3 | 30 | 80 | [5 empty] | Copy of official tap setting GISTET KEMBANGAN BAY BALARAJA main B_toshiba GRL200.pdf | 2021-05-21 |  | 9.92 | 86 | 1 | 0.3 | 3 | 30 | 80 | [6 empty] | 0
PHT.183 | 183 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 2000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | NR | PCS-931 | NRJB20155116B0340[FE4878] | NUMERIK | 2019 |  | 0 | 0 | 1 | 0 | 0 | - | - | [8 empty] | 1.955 | 85 | 1 | 0.2 | 1 | - | - | [6 empty] | 30.14
PHT.184 | 184 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 2000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | NR | PCS-931 | NRJB2015516B0310[EF4AA8] | NUMERIK | 2019 |  | 0 | 0 | 1 | 0 | 0 | - | - | [8 empty] | 1.955 | 85 | 1 | 0.2 | 1 | - | - | [6 empty] | 30.14

## Rekap1 (hidden)
DATA RELE
|  | total | DIFF 500 | Main A | Main B | LCD 500 | Main A | Main B | Distance 500 | DIFF 150 | LCD 150 | Distance 150 | Diff Pilot | OCR PHT | OCR 150 | OCR 20 | SBEF | OCR
| ABB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Alsthom | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Alstom | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Areva | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Asea | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Schneider | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SEG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Siemens | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toshiba | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| No MERK | 4 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0
|  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0
RELE MAIN PROT 500 kV | [10 empty] | Numerik |  | Elektromekanik
|  | Numerik | Elektromekanik |  |  | Belum Ada |  |  | Kontrak KI 2018 |  | Main A | Main B | Main A | Main B
| DIFF | 0 | 0 |  |  | 0 |  |  | 0
| LCD | 0 | 0 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| Distance | 0 | 0 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
RELE MAIN PROT 150 kV
|  | Numerik | Elektromekanik |  |  | Belum Ada |  |  | Kontrak KI 2018 | Kontrak UPT 2019
| DIFF | 0 | 0 |  |  | 0 |  |  | 0 | 0
| LCD | 0 | 0 |  |  | 0 |  |  | 0 | 0
| Distance | 0 | 0 |  |  | 0 |  |  | 0 | 0
| Diff Pilot | 0 | 0 |  |  | 0 |  |  | 0 | 0
|  | Numerik | Kontrak KI 2018
| DIFF Pilot | 0 | 0
RELE BACKUP PROT | [10 empty] | Kontrak penggantian |  |  |  | Total
|  | Numerik | Elektromekanik |  |  | Belum Ada |  |  | Obsolet | Rusak | Kontrak KI 2018 | Kontrak UPT 2019 | Kontrak Distribusi | Belum | Numerik
| OCR PHT | 0 | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OCR 150 kV | 0 | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OCR 20 kV | 0 | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Numerik | Kontrak KI 2018 |  |  | Kontrak UPT 2019 |  |  | Kontrak Distribusi | Belum
| OCR 150 kV | 0 | 0 |  |  | 0 |  |  | 0 | 0
|  | Numerik | Kontrak KI 2018 |  |  | Kontrak UPT 2019 |  |  | Kontrak Distribusi | Belum
| OCR 20 kV | 0 | 0 |  |  | 0 |  |  | 0 | 0
|  | Numerik | Elektromekanik
| SBEF | 0 | 0

## Pivot Table 1 (hidden)
Distance 500 Main A |  |  |  |  | Distance 500 Main B
#REF! |  |  |  |  | #REF!
LCD 500 Main A |  |  |  |  | LCD 500 Main B
#REF! |  |  |  |  | #REF!
LCD 150 Main A |  |  |  |  | LCD 150 Main B
#REF! |  |  |  |  | #REF!
Distance
DIFF PILOT Main A |  |  |  |  | DIFF PILOT Main B
| COUNTA of |  |  |  |  | COUNTA of
Numerik | 4 |  |  |  | Numerik | 4
Grand Total | 4 |  |  |  | Grand Total | 4
BUSPRO
COUNTA of
0
Elektromekanik | 5
Numerik | 27
Tidak Ada | 1
Grand Total | 33
OCR PHT
REKAP PHT
|  |  | TOTAL | NUMERIK | ELEKTROMEKANIK | 9 | 6 | 1
|  | MAIN PROT | 0 | 0 |  | 0 | 0 | 0
|  | BACKUP | 0 |  |  |  |  | 0

## DIFF Pilot (hidden)
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
NO | GI / GIS | BAY | BAY | ULTG | GI / GIS | BAY | Sirkit | RATIO CT | DIFFERENTIAL PILOT 1 | [8 empty] | DIFFERENTIAL PILOT 2
[9 empty] | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SETTING |  |  |  | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SETTING
[14 empty] | In | Rset | Iset | waktu | [5 empty] | In | Rset | Iset | waktu
1 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0013 - PHT 150kV NEW SENAYAN #1 | PHT 150kV NEW SENAYAN #1 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN | #1 | 1000 / 5 | Areva | MiCom P521 | 0807305 | Numerik |  | 5 | - | 1 | instant | Areva | MiCom P521 | 0807302 | Numerik |  | 5 | - | 1 | instant
2 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0008 - PHT 150kV NEW SENAYAN #2 | PHT 150kV NEW SENAYAN #2 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN | #2 | 1000 / 5 | Areva | MiCom P521 | 0807303 | Numerik |  | 5 | - | 1 | instant | Areva | MiCom P521 | 0807304 | Numerik |  | 5 | - | 1 | instant
3 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0007 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN | #1 | 1000 / 5 | Areva | MiCom P521 | 0507874 | Numerik |  | 5 | - | 1 | instant | Areva | MiCom P521 | 0507876 | Numerik |  | 5 | - | 1 | instant
4 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0005 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN | #2 | 1000 / 5 | Areva | MiCom P521 | 0507875 | Numerik |  | 5 | - | 1 | instant | Areva | MiCom P521 | 0507877 | Numerik |  | 5 | - | 1 | instant

## DIST
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | SIRKIT | RATIO CT - MPU | RATIO PT | RELAY | HELPER ASET |  | MERK | TIPE | NO. SERI | JENIS RELE | TH OPERASI | DIST | [20 empty] | DIST
[9 empty] | GI/GIS | BAY | [5 empty] | TAP SET | SETTING IMPEDANSI | [7 empty] | SETTING WAKTU |  |  | DEF |  |  | SKEMA TP |  |  |  | SOTF | TOR | SET RELAY | SETTING IMPEDANSI | [8 empty] | SETTING WAKTU |  |  | DEF |  |  | SKEMA TP |  |  |  | SOTF | TOR
[17 empty] | CHAR |  | Z1 |  | Z2 |  | Z3 |  | t1 | t2 | t3 | Is | t | sudut | AIDED DEF | WAKTU KERJA | (POTT/ PUTT/ Blocking) | CURRENT REVERSAL | INIT FROM | INIT FROM |  | CONFIG DIST | Source : Form Implementasi Scanning | [7 empty] | t1 | t2 | t3 | Is | t | sudut | AIDED DEF | WAKTU KERJA | (POTT/ PUTT/ Blocking) | CURRENT REVERSAL | INIT FROM | INIT FROM
[39 empty] | CHAR |  | Z1 |  | Z2 |  | Z3
[17 empty] | ph-ph | ph-gnd | ph-ph | ph-gnd | ph-ph | ph-gnd | ph-ph | ph-gnd | [14 empty] | ph-ph | ph-gnd | ph-ph | ph-gnd | ph-ph | ph-gnd | ph-ph | ph-gnd
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59
PHT.01 | 1 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV ANCOL #1 | GE | MICOM P545 | 36039274/03/22 | NUMERIK | 2022 |  |  |  | 0.263 | 0.263 | 0.403 | 0.403 | 0.951 | 0.951 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.264 | 0.264 | 0.404 | 0.404 | 0.952 | 0.952 | 0 | 0.4 | 1.6
PHT.02 | 2 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV ANCOL #2 | GE | MICOM P545 | 36039272/03/22 | NUMERIK | 2022 |  |  |  | 0.263 | 0.263 | 0.403 | 0.403 | 0.951 | 0.951 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.03 | 3 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KARET LAMA #1 | GE | MICOM P443 | 34424435/04/18 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 1.036 | 1.036 | 1.554 | 1.554 | 2.826 | 2.826 | 0 | 0.8 | 1.6
PHT.04 | 4 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KARET LAMA #2 | GE | MICOM P443 | 34424434/04/18 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 1.036 | 1.036 | 1.554 | 1.554 | 2.826 | 2.826 | 0 | 0.8 | 1.6
PHT.05 | 5 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KETAPANG #1 | ALSTOM | MICOM P545 | 34421606/04/18 | NUMERIK | 2021 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 0.194 | 0.194 | 0.292 | 0.292 | 0.442 | 0.442 | 0 | 0.4 | 1.6
PHT.06 | 6 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV KETAPANG #2 | ALSTOM | MICOM P545 | 34421607/04/18 | NUMERIK | 2021 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 0.186 | 0.186 | 0.334 | 0.334 | 0.556 | 0.556 | 0 | 0.4 | 1.6
PHT.07 | 7 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #1 | SIEMENS | 7SD61 | BF0807106719 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.08 | 8 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #2 | SIEMENS | 7SD61 | BF0807106718 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.09 | 9 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #1 | SIEMENS | 7SL87 | BM1712005923 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.10 | 10 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #2 | SIEMENS | 7SL87 | BM1712005927 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.11 | 11 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV LONTAR #1 | GE | MICOM P446 | 34465139/05/18 | NUMERIK | 2021 |  |  |  | 15.519 | 15.519 | 25.819 | 25.819 | 42.591 | 42.591 | 0 | 0.4 | 0 | [10 empty] | Enabled |  |  | 15.93 | 15.93 | 23.9 | 23.9 | 43.21 | 43.21 | 0 | 0.4 | 1.6
PHT.12 | 12 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV LONTAR #2 | GE | MICOM P446 | 34465154/05/18 | NUMERIK | 2021 |  |  |  | 15.519 | 15.519 | 25.819 | 25.819 | 42.591 | 42.591 | 0 | 0.4 | 0 | [10 empty] | Enabled |  |  | 15.93 | 15.93 | 23.9 | 23.9 | 43.2 | 43.2 | 0 | 0.4 | 1.6
PHT.13 | 13 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV TELUK NAGA #1 | GE | MICOM P546 | 34465138/05/18 | NUMERIK | 2021 |  |  |  | 3.719 | 3.719 | 8.15 | 8.15 | 13.887 | 13.887 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 3.72 | 3.72 | 8.15 | 8.15 | 13.89 | 13.89 | 0 | 0.4 | 1.6
PHT.14 | 14 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GID 150KV DADAP | PHT 150kV TELUK NAGA #2 | GE | MICOM P546 | 34465149/05/18 | NUMERIK | 2021 |  |  |  | 3.719 | 3.719 | 8.15 | 8.15 | 13.887 | 13.887 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 3.72 | 3.72 | 8.15 | 8.15 | 13.89 | 13.89 | 0 | 0.4 | 1.6
PHT.15 | 15 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 2500/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #1 | ALSTOM | MICOM P545 | 34923699/11/19 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.16 | 16 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 2500/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #2 | ALSTOM | MICOM P545 | 32197930/06/12 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.17 | 17 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #1 | AREVA | MICOM P521 | 1307744 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | N/A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.18 | 18 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #2 | ALSTOM | MICOM P543 | 31995324/12/11 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.19 | 19 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #1 | SIEMENS | 7SD61 | BF0807106717 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.20 | 20 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #2 | SIEMENS | 7SD61 | BF0807106723 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.21 | 21 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#1 | #1 | 1200/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #1 | GE | MICOM P546 | 37123537/07/25 | NUMERIK | 2026 |  |  |  | 0.21 | 0.21 | 0.31 | 0.31 | 0.43 | 0.43 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.21 | 0.21 | 0.31 | 0.31 | 0.43 | 0.43 | 0 | 0.4 | 1.6
PHT.22 | 22 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#2 | #2 | 1200/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #2 | GE | MICOM P546 | 37362776/03/26 | NUMERIK | 2026 |  |  |  | 0.21 | 0.21 | 0.31 | 0.31 | 0.43 | 0.43 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.21 | 0.21 | 0.31 | 0.31 | 0.43 | 0.43 | 0 | 0.4 | 1.6
PHT.23 | 23 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #1 | AREVA | MICOM P521 | 1307747 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | N/A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.24 | 24 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #2 | AREVA | MICOM P543 | 31507153/09/10 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.25 | 25 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #1 | SIEMENS | 7SL87 | BM1712005935 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | ON |  |  | 2.5 | 2.5 | 5 | 5 | 10 | 10 | 0 | 0.3 | 0.6
PHT.26 | 26 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #2 | SIEMENS | 7SL87 | BM1712005931 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | ON |  |  | 2.5 | 2.5 | 5 | 5 | 10 | 10 | 0 | 0.3 | 0.6
PHT.27 | 27 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #1 | ABB | RED670 | T1645093 | NUMERIK | 2019 |  |  |  | 2.073 | 2.073 | 3.11 | 3.11 | 22.212 | 22.212 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.28 | 28 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #2 | ABB | RED670 | T1645092 | NUMERIK | 2019 |  |  |  | 2.073 | 2.073 | 3.11 | 3.11 | 22.212 | 22.212 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.29 | 29 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #1 | ALSTOM | MICOM P545 | 32197932/07/12 | NUMERIK | 2022 |  |  |  | 9.187 | 9.187 | 16.696 | 16.696 | 27.861 | 27.861 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 9.19 | 9.19 | 16.7 | 16.7 | 27.86 | 27.86 | 0 | 0.4 | 1.6
PHT.30 | 30 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #2 | ALSTOM | MICOM P545 | 34164813/08/17 | NUMERIK | 2019 |  |  |  | 9.187 | 9.187 | 16.696 | 16.696 | 27.861 | 27.861 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 9.19 | 9.19 | 16.7 | 16.7 | 27.86 | 27.86 | 0 | 0.4 | 1.6
PHT.31 | 31 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#1 | #1 | 1600/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #1 | SIEMENS | 7SL87 | BM1809009341 | NUMERIK | 2019 |  |  |  | 0.479 | 0.479 | 1.718 | 1.718 | 3.043 | 3.043 | 0 | 0.4 | 1.6 | [13 empty] | 0.479 | 0.479 | 1.718 | 1.718 | 3.043 | 3.043 | 0 | 0.4 | 1.6
PHT.32 | 32 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#2 | #2 | 1600/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #2 | SIEMENS | 7SL87 | BM1909000269 | NUMERIK | 2020 |  |  |  | 0.479 | 0.479 | 1.718 | 1.718 | 3.043 | 3.043 | 0 | 0.4 | 1.6 | [13 empty] | 0.479 | 0.479 | 1.718 | 1.718 | 3.043 | 3.043 | 0 | 0.4 | 1.6
PHT.33 | 33 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV TOMANG #1 | SCHNEIDER | MICOM P543 | 753937F | NUMERIK | 2021 |  |  |  | 0.664 | 0.664 | 1.148 | 1.148 | 2.38 | 2.38 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 0.66 | 0.66 | 1.19 | 1.19 | 2.38 | 2.38 | 0 | 0.4 | 1.2
PHT.34 | 34 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL | PHT 150kV TOMANG #2 | SCHNEIDER | MICOM P543 | 753791F | NUMERIK | 2021 |  |  |  | 0.664 | 0.664 | 1.148 | 1.148 | 2.38 | 2.38 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 0.66 | 0.66 | 1.19 | 1.19 | 1.99 | 1.99 | 0 | 0.4 | 1.2
PHT.35 | 35 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #1 | SIEMENS | 7SL87 | BM1804005484 | NUMERIK | 2019 |  |  |  | 1.937 | 1.937 | 2.905 | 2.905 | 28.375 | 28.375 | 0 | 0.8 | 1.6 | [13 empty] | 1.937 | 1.937 | 2.905 | 2.905 | 28.375 | 28.375 | 0 | 0.8 | 1.6
PHT.36 | 36 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #2 | SIEMENS | 7SL87 | BM1804005475 | NUMERIK | 2020 |  |  |  | 1.937 | 1.937 | 2.905 | 2.905 | 28.375 | 28.375 | 0 | 0.8 | 1.6 | [13 empty] | 1.937 | 1.937 | 2.905 | 2.905 | 28.375 | 28.375 | 0 | 0.8 | 1.6
PHT.37 | 37 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #1 | SIEMENS | 7SL87 | BM1804005481 | NUMERIK | 2019 |  |  |  | 0.599 | 0.599 | 1.078 | 1.078 | 1.796 | 1.796 | 0 | 0.4 | 1.6 | [13 empty] | 0.599 | 0.599 | 1.078 | 1.078 | 1.796 | 1.796 | 0 | 0.4 | 1.6
PHT.38 | 38 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #2 | SIEMENS | 7SL87 | BM1804005478 | NUMERIK | 2020 |  |  |  | 0.599 | 0.599 | 1.078 | 1.078 | 1.796 | 1.796 | 0 | 0.4 | 1.6 | [13 empty] | 0.599 | 0.599 | 1.078 | 1.078 | 1.796 | 1.796 | 0 | 0.4 | 1.6
PHT.39 | 39 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #1 | ALSTOM | MICOM P545 | 34665002/12/18 | NUMERIK | 2019 |  |  |  | 0.125 | 0.125 | 0.187 | 0.187 | 0.948 | 0.948 | 0 | 0.4 | 1.6 | [10 empty] | Disable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.40 | 40 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #2 | ALSTOM | MICOM P545 | 34482258/06/18 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.41 | 41 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#1 | #1 | 500/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #1 | ALSTOM | MICOM P545 | 34923727/11/19 | NUMERIK | 2020 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.42 | 42 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#2 | #2 | 500/5 | 150 kV/100 V | MPU | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #2 | ALSTOM | MICOM P545 | 34485202/06/18 | NUMERIK | 2020 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.43 | 43 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #1 | ALSTOM | MICOM P545 | 34724838/02/19 | NUMERIK | 2022 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.44 | 44 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #2 | ALSTOM | MICOM P545 | 34724836/02/19 | NUMERIK | 2022 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.45 | 45 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #1 | ALSTOM | MICOM P545 | 34724837/02/19 | NUMERIK | 2022 |  |  |  | 12.657 | 12.657 | 22.457 | 22.457 | 37.36 | 37.36 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.46 | 46 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #2 | ALSTOM | MICOM P545 | 34724835/02/19 | NUMERIK | 2022 |  |  |  | 12.657 | 12.657 | 22.457 | 22.457 | 37.36 | 37.36 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.47 | 47 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #1 | GE | MICOM P546 | 37132771/07/25 | NUMERIK | 2025 |  |  |  | 0.12 | 0.12 | 0.18 | 0.18 | 0.33 | 0.33 | 0 | 0.4 | 1.6 | [10 empty] | Disabled |  |  | 0.12 | 0.12 | 0.18 | 0.18 | 0.33 | 0.33 | 0 | 0.4 | 1.6
PHT.48 | 48 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #2 | GE | MICOM P546 | 37132773/07/25 | NUMERIK | 2025 |  |  |  | 0.12 | 0.12 | 0.18 | 0.18 | 0.33 | 0.33 | 0 | 0.4 | 1.6 | [10 empty] | Disabled |  |  | 0.12 | 0.12 | 0.18 | 0.18 | 0.33 | 0.33 | 0 | 0.4 | 1.6
PHT.49 | 49 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #1 | ALSTOM | MICOM P545 | 33493424/11/15 | NUMERIK | 2019 |  |  |  | 0.944 | 0.944 | 1.846 | 1.846 | 3.109 | 3.109 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.94 | 0.94 | 1.85 | 1.85 | 3.11 | 3.11 | 0 | 0.4 | 1.6
PHT.50 | 50 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #2 | ALSTOM | MICOM P545 | 33493423/11/15 | NUMERIK | 2019 |  |  |  | 0.944 | 0.944 | 1.846 | 1.846 | 3.109 | 3.109 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.94 | 0.94 | 1.85 | 1.85 | 3.11 | 3.11 | 0 | 0.4 | 1.6
PHT.51 | 51 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #1 | NR | PCS-931 | NRJB2015511480260 | NUMERIK | 2021 |  |  |  | 0.24 | 0.24 | 0.433 | 0.433 | 0.721 | 0.721 | 0 | 0.4 | 1.2 | [13 empty] | 0.24 | 0.24 | 0.433 | 0.433 | 0.721 | 0.721 | 0 | 0.4 | 1.2
PHT.52 | 52 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #2 | ALSTOM | MICOM P545 | 34733776/03/19 | NUMERIK | 2021 |  |  |  | 0.24 | 0.24 | 0.433 | 0.433 | 1.73 | 1.73 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.24 | 0.24 | 0.43 | 0.43 | 0.72 | 0.72 | 0 | 0.4 | 1.6
PHT.53 | 53 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #1 | ALSTOM | MICOM P545 | 32288899/09/12 | NUMERIK | 2016 |  |  |  | 12.249 | 12.249 | 18.374 | 18.374 | 26.762 | 26.762 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 12.25 | 12.25 | 18.37 | 18.37 | 26.76 | 26.76 | 0 | 0.4 | 1.6
PHT.54 | 54 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #2 | ALSTOM | MICOM P545 | 32288900/09/12 | NUMERIK | 2016 |  |  |  | 12.249 | 12.249 | 18.374 | 18.374 | 26.762 | 26.762 | 0 | 0.4 | 1.6 | [10 empty] | ENABLE |  |  | 12.25 | 12.25 | 18.37 | 18.37 | 26.76 | 26.76 | 0 | 0.4 | 1.6
PHT.55 | 55 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #1 | ALSTOM | MICOM P545 | 197931U | NUMERIK | 2016 |  |  |  | 12.516 | 12.516 | 18.774 | 18.774 | 19.41 | 19.41 | 0 | 0.8 | 1.6 | [10 empty] | ENABLE |  |  | 12.66 | 12.66 | 18.99 | 18.99 | 19.09 | 19.09 | 0 | 0.8 | 1.6
PHT.56 | 56 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #2 | ALSTOM | MICOM P545 | 32197933/06/12 | NUMERIK | 2016 |  |  |  | 12.516 | 12.516 | 18.774 | 18.774 | 19.41 | 19.41 | 0 | 0.8 | 1.6 | [10 empty] | ENABLE |  |  | 12.66 | 12.66 | 18.99 | 18.99 | 19.09 | 19.09 | 0 | 0.8 | 1.6
PHT.57 | 57 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV TOMANG | PHT 150kV GROGOL #1 | ALSTOM | MICOM P543 | 39652554/04/18 | NUMERIK | 2021 |  |  |  | 0.664 | 0.664 | 1.148 | 1.148 | 2.38 | 2.38 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 0.66 | 0.66 | 1.15 | 1.15 | 2.38 | 2.38 | 0 | 0.4 | 1.2
PHT.58 | 58 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV TOMANG | PHT 150kV GROGOL #2 | ALSTOM | MICOM P543 | 37055880/10/18 | NUMERIK | 2021 |  |  |  | 0.664 | 0.664 | 1.148 | 1.148 | 2.38 | 2.38 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 0.66 | 0.66 | 1.15 | 1.15 | 2.38 | 2.38 | 0 | 0.4 | 1.2
PHT.59 | 59 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #1 | NR | PCS-931 | NRJB20155116B0230[CE4B8B] | NUMERIK | 2021 |  |  |  | 0.24 | 0.24 | 0.982 | 0.982 | 5.018 | 5.018 | 0 | 0.4 | 1.6 | [13 empty] | 0.24 | 0.24 | 0.982 | 0.982 | 5.108 | 5.108 | 0 | 0.4 | 1.6
PHT.60 | 60 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #2 | GE | MICOM P545 | 34733777/03/19 | NUMERIK | 2021 |  |  |  | 0.24 | 0.24 | 0.982 | 0.982 | 5.018 | 5.018 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.24 | 0.24 | 0.98 | 0.98 | 5.02 | 5.02 | 0 | 0.4 | 1.6
PHT.61 | 61 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | ABB | RED670 | T2136184 | NUMERIK |  |  |  |  | 2.139 | 2.139 | 3.209 | 3.209 | 14.682 | 14.682 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.62 | 62 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | ABB | RED670 | T2136186 | NUMERIK |  |  |  |  | 2.139 | 2.139 | 3.209 | 3.209 | 14.682 | 14.682 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.63 | 63 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | SIEMENS | 7SL87 | BM2110007783 | NUMERIK |  |  |  |  | 1.711 | 1.711 | 2.567 | 2.567 | 11.746 | 11.746 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.64 | 64 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | SIEMENS | 7SL87 | BM2110006379 | NUMERIK |  |  |  |  | 1.711 | 1.711 | 2.567 | 2.567 | 11.746 | 11.746 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.65 | 65 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 |  | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | ABB | RED670 | T2136180 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.66 | 66 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 |  | 500 kV/100 V | MPU-A | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | ABB | RED670 | T2136185 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.67 | 67 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 |  | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | SIEMENS | 7SL87 | BM2110006364 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.68 | 68 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 |  | 500 kV/100 V | MPU-B | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | SIEMENS | 7SL87 | BM2110006369 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.69 | 69 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV CIKUPA #1 | ALSTOM | MICOM P545 | 34721258/02/19 | NUMERIK | 2019 |  |  |  | 1.808 | 1.808 | 3.186 | 3.186 | 5.986 | 5.986 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 1.809 | 1.809 | 3.16 | 3.16 | 5.989 | 5.989 | 0 | 0.4 | 1.6
PHT.70 | 70 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#2 | #2 | 3200/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV CIKUPA #2 | ALSTOM | MICOM P545 | 34486826/06/18 | NUMERIK | 2019 |  |  |  | 4.558 | 4.558 | 6.837 | 6.837 | 14.593 | 14.593 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 2.85 | 2.85 | 5.05 | 5.05 | 9.511 | 9.511 | 0 | 0.4 | 1.6
PHT.71 | 71 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 3200/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #1 | ALSTOM | MICOM P545 | 34486816/06/18 | NUMERIK | 2019 |  |  |  | 0.723 | 0.723 | 1.559 | 1.559 | 2.652 | 2.652 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.72 | 0.72 | 1.56 | 1.56 | 2.649 | 2.649 | 0 | 0.4 | 1.6
PHT.72 | 72 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #2 | ALSTOM | MICOM P545 | 34721255/02/19 | NUMERIK | 2019 |  |  |  | 0.452 | 0.452 | 0.974 | 0.974 | 1.658 | 1.658 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.45 | 0.45 | 0.97 | 0.97 | 1.649 | 1.649 | 0 | 0.4 | 1.6
PHT.73 | 73 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | #1 | 2000/1 | 150 kV/100 V | MPU | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | GE | L90 | AA2C17001630 | NUMERIK | 2018 |  |  |  | 1.772 | 1.772 | 3.425 | 3.425 | 5.757 | 5.757 | 0 | 0.4 | 1.6 | [13 empty] | 1.77 | 1.77 | 3.42 | 3.42 | 5.75 | 5.75 | 0 | 0.4 | 1.6
PHT.74 | 74 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | #1 | 2000/1 | 150 kV/100 V | MPU | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | ALSTOM | MICOM P543 | 32069228/02/12 | NUMERIK | 2021 |  |  |  | 1.48 | 1.48 | 2.326 | 2.326 | 3.807 | 3.807 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 1.48 | 1.48 | 2.33 | 2.33 | 3.81 | 3.81 | 0 | 0.4 | 1.6
PHT.75 | 75 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV TANGERANG BARU | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV ITS | PHT 150kV TANGERANG BARU | GE | MICOM P545 | 35301414/03/12 | NUMERIK | 2021 |  |  |  | 3.361 | 3.361 | 10.399 | 10.399 | 24.342 | 24.342 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.76 | 76 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV CENGKARENG BARU | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV ITS | PHT 150kV CENGKARENG BARU | AREVA | MICOM P543 | 3379380/04/09 | NUMERIK | 2021 |  |  |  | 5.505 | 5.505 | 8.257 | 8.257 | 11.692 | 11.692 | 0 | 0.8 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.77 | 77 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV KONSUMEN | #1 | 300/1 | 150 kV/100 V | MPU | GI 150KV ITS | PHT 150kV KONSUMEN | SIEMENS | 7SL87 | BM2102005251 | NUMERIK | 2021 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.78 | 78 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#1 | #1 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV CIKUPA #1 | ALSTOM | MICOM P442 | 31830604/07/11 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.79 | 79 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#2 | #2 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV CIKUPA #2 | ALSTOM | MICOM P442 | 31830599/07/11 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.80 | 80 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#1 | #1 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV JATAKE BARU #1 | NR | PCS-931 | NRJB20155119B0540 | NUMERIK | 2021 |  |  |  | 0.171 | 0.171 | 0.436 | 0.436 | 1.111 | 1.111 | 0 | 0.4 | 1.2 | [13 empty] | 0.189 | 0.189 | 0.497 | 0.497 | 1.127 | 1.127 | 0 | 0.4 | 1.6
PHT.81 | 81 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#2 | #2 | 1600/5 | 150 kV/100 V | MPU | GI 150KV JATAKE | PHT 150kV JATAKE BARU #2 | NR | PCS-931 | NRJB20155119B0550 | NUMERIK | 2021 |  |  |  | 0.171 | 0.171 | 0.436 | 0.436 | 1.111 | 1.111 | 0 | 0.4 | 1.2 | [13 empty] | 0.189 | 0.189 | 0.497 | 0.497 | 1.127 | 1.127 | 0 | 0.4 | 1.6
PHT.82 | 82 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | NR | PCS-931 | NRJB2015511830010 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.83 | 83 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | NR | PCS-931 | NRJB2015511830040 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0.067 | 0.067 | 0.121 | 0.121 | 0.202 | 0.202 | 0 | 0.4 | 1.6
PHT.84 | 84 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | NR | PCS-931 | NRJB2015511830020 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.85 | 85 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | NR | PCS-931 | NRJB2015511830030 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0.067 | 0.067 | 0.121 | 0.121 | 0.202 | 0.202 | 0 | 0.4 | 1.6
PHT.86 | 86 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | NR | PCS-931 | NRJB2015511830070 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.87 | 87 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 1000/1 | 150 kV/100 V | MPU-A | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | NR | PCS-931 | NRJB2015511830100 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.88 | 88 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | NR | PCS-931 | NRJB2015511830080 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.89 | 89 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 1000/1 | 150 kV/100 V | MPU-B | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | NR | PCS-931 | NRJB2015511830090 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.90 | 90 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #1 | NR | PCS-931 | NRJB2029221960030 | NUMERIK | 2021 |  |  |  | 4.664 | 4.664 | 7.956 | 7.956 | 17.278 | 17.278 | 0 | 0.4 | 1.6 | [13 empty] | 4.664 | 4.664 | 7.956 | 7.956 | 17.278 | 17.278 | 0 | 0.4 | 1.6
PHT.91 | 91 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #2 | NR | PCS-931 | NRJB2029221960100 | NUMERIK | 2021 |  |  |  | 4.664 | 4.664 | 7.956 | 7.956 | 17.278 | 17.278 | 0 | 0.4 | 1.6 | [13 empty] | 4.664 | 4.664 | 7.956 | 7.956 | 17.278 | 17.278 | 0 | 0.4 | 1.6
PHT.92 | 92 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #1 | NR | PCS-931 | NRJB2006301870170 | NUMERIK | 2021 |  |  |  | 7.557 | 7.557 | 19.917 | 19.917 | 37.368 | 37.368 | 0 | 0.4 | 1.6 | [13 empty] | 7.557 | 7.557 | 19.917 | 19.917 | 37.368 | 37.368 | 0 | 0.4 | 1.6
PHT.93 | 93 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #2 | NR | PCS-931 | NRJB2015511680190[A74B17] | NUMERIK | 2021 |  |  |  | 7.557 | 7.557 | 19.917 | 19.917 | 37.368 | 37.368 | 0 | 0.4 | 1.6 | [13 empty] | 7.557 | 7.557 | 19.917 | 19.917 | 37.368 | 37.368 | 0 | 0.4 | 1.6
PHT.94 | 94 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #1 | NR | PCS-931 | NRJB2029221960020 | NUMERIK | 2021 |  |  |  | 2.776 | 2.776 | 5.628 | 5.628 | 9.516 | 9.516 | 0 | 0.4 | 1.2 | [13 empty] | 2.776 | 2.776 | 5.628 | 5.628 | 9.516 | 9.516 | 0 | 0.4 | 1.2
PHT.95 | 95 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #2 | NR | PCS-931 | NRJB2029221960010 | NUMERIK | 2021 |  |  |  | 2.776 | 2.776 | 5.628 | 5.628 | 9.516 | 9.516 | 0 | 0.4 | 1.2 | [13 empty] | 2.776 | 2.776 | 5.628 | 5.628 | 9.516 | 9.516 | 0 | 0.4 | 1.2
PHT.96 | 96 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #1 | GE | MICOM P546 | 36265528/12/22 | NUMERIK | 2021 |  |  |  | 9.027 | 9.027 | 14.142 | 14.142 | 21.532 | 21.532 | 0 | 0.4 | 1.6 | [10 empty] | Enable |  |  | 9.03 | 9.03 | 14.14 | 14.14 | 21.53 | 21.53 | 0 | 0.4 | 1.6
PHT.97 | 97 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #2 | GE | MICOM P546 | 36265524/12/22 | NUMERIK | 2021 |  |  |  | 9.027 | 9.027 | 14.142 | 14.142 | 21.532 | 21.532 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 9.03 | 9.03 | 14.14 | 14.14 | 21.53 | 21.53 | 0 | 0.4 | 1.6
PHT.98 | 98 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV ITS | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV ITS | GE | MICOM P545 | 35298236/03/21 | NUMERIK | 2021 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 2.52 | 2.52 | 5.82 | 5.82 | 9.97 | 9.97 | 0 | 0.4 | 1.6
PHT.99 | 99 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | AREVA | MICOM P543 | 3379379/05/09 | NUMERIK | 2021 |  |  |  | 8.643 | 8.643 | 15.13 | 15.13 | 28.221 | 28.221 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 6.6 | 6.6 | 9.9 | 9.9 | 12.47 | 12.47 | 0 | 0.4 | 1.6
PHT.100 | 100 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV DADAP #1 | AREVA | MICOM P546 | 34434876/05/18 | NUMERIK |  |  |  |  | 2.789 | 2.789 | 12.1 | 12.1 | 21.642 | 21.642 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 2.79 | 2.79 | 12.1 | 12.1 | 21.64 | 21.64 | 0 | 0.4 | 1.6
PHT.101 | 101 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV DADAP #2 | AREVA | MICOM P546 | 34450419/05/18 | NUMERIK |  |  |  |  | 2.789 | 2.789 | 12.1 | 12.1 | 21.642 | 21.642 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 2.79 | 2.79 | 12.1 | 12.1 | 21.64 | 21.64 | 0 | 0.4 | 1.6
PHT.102 | 102 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#1 | #1 | 1600/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #1 | GE | MICOM P546 |  | NUMERIK | 2018 |  |  |  | 2.22 | 2.22 | 3.32 | 3.32 | 4.52 | 4.52 | 0 | 0.8 | 1.2 | [10 empty] | Enabled |  |  | 2.22 | 2.22 | 3.32 | 3.32 | 4.52 | 4.52 | 0 | 0.8 | 1.2
PHT.103 | 103 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#2 | #2 | 1600/1 | 150 kV/100 V | MPU | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #2 | GE | MICOM P546 |  | NUMERIK | 2018 |  |  |  | 2.22 | 2.22 | 3.32 | 3.32 | 4.52 | 4.52 | 0 | 0.8 | 1.2 | [10 empty] | Enabled |  |  | 2.22 | 2.22 | 3.32 | 3.32 | 4.52 | 4.52 | 0 | 0.8 | 1.2
PHT.104 | 104 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #1 | NR | PCS-931 | NRJB20155119B0340 | NUMERIK | 2021 |  |  |  | 1.067 | 1.067 | 1.6 | 1.6 | 4.874 | 4.874 | 0 | 0.8 | 1.2 | [13 empty] | 0.943 | 0.943 | 1.415 | 1.415 | 4.688 | 4.688 | 0 | 0.8 | 1.6
PHT.105 | 105 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #2 | NR | PCS-931 | NRJB20155119B0050 | NUMERIK | 2021 |  |  |  | 1.067 | 1.067 | 1.6 | 1.6 | 4.874 | 4.874 | 0 | 0.8 | 1.2 | [13 empty] | 0.943 | 0.943 | 1.415 | 1.415 | 4.688 | 4.688 | 0 | 0.8 | 1.6
PHT.106 | 106 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #1 | NR | PCS-931 | NRJB20155119B0370 | NUMERIK | 2021 |  |  |  | 2.076 | 2.076 | 7.348 | 7.348 | 12.998 | 12.998 | 0 | 0.4 | 1.6 | [13 empty] | 2.076 | 2.076 | 7.348 | 7.348 | 12.998 | 12.998 | 0 | 0.4 | 1.6
PHT.107 | 107 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #2 | NR | PCS-931 | NRJB20155119B0360 | NUMERIK | 2021 |  |  |  | 2.076 | 2.076 | 7.348 | 7.348 | 12.998 | 12.998 | 0 | 0.4 | 1.6 | [13 empty] | 2.076 | 2.076 | 7.348 | 7.348 | 12.998 | 12.998 | 0 | 0.4 | 1.6
PHT.108 | 108 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #1 | SCHNEIDER | MICOM P443 | 39615255/07/17 | NUMERIK | 2021 |  |  |  | 7.557 | 7.557 | 11.335 | 11.335 | 18.331 | 18.331 | 0 | 0.4 | 0 | [10 empty] | Enabled |  |  | 7.56 | 7.56 | 11.34 | 11.34 | 18.33 | 18.33 | 0 | 0.4 | 1.6
PHT.109 | 109 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #2 | SCHNEIDER | MICOM P443 | 39619256/07/17 | NUMERIK | 2021 |  |  |  | 7.557 | 7.557 | 11.335 | 11.335 | 18.331 | 18.331 | 0 | 0.4 | 0 | [10 empty] | Enabled |  |  | 7.56 | 7.56 | 11.34 | 11.34 | 18.33 | 18.33 | 0 | 0.4 | 1.6
PHT.110 | 110 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV DADAP #1 | ALSTOM | MICOM P446 | 34389472/03/18 | NUMERIK |  |  |  |  | 11.639 | 11.639 | 17.459 | 17.459 | 21.642 | 21.642 | 0 | 0.4 | 0 | [10 empty] | Enabled |  |  | 11.95 | 11.95 | 17.93 | 17.93 | 22.11 | 22.11 | 0 | 0.4 | 1.6
PHT.111 | 111 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV DADAP #2 | ALSTOM | MICOM P446 | 34486172/06/18 | NUMERIK |  |  |  |  | 11.639 | 11.639 | 17.459 | 17.459 | 21.642 | 21.642 | 0 | 0.4 | 0 | [10 empty] | Enabled |  |  | 11.95 | 11.95 | 17.93 | 17.93 | 22.11 | 22.11 | 0 | 0.4 | 1.6
PHT.112 | 112 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #1 | GE | MICOM P546 | 36265529/12/22 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.113 | 113 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#2 | #2 | 3000/1 | 150 kV/100 V | MPU | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #2 | GE | MICOM P546 | 36265525/12/22 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.114 | 114 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #1 | GE | MICOM P545 | 36039278/03/22 | NUMERIK |  |  |  |  | 1.018 | 1.018 | 1.527 | 1.527 | 2.699 | 2.699 | 0 | 0.8 | 1.6 | [10 empty] | Enabled |  |  | 1.018 | 1.018 | 1.528 | 1.528 | 2.7 | 2.7 | 0 | 0.8 | 1.6
PHT.115 | 115 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #2 | GE | MICOM P545 | 36039283/03/22 | NUMERIK |  |  |  |  | 1.018 | 1.018 | 1.527 | 1.527 | 2.699 | 2.699 | 0 | 0.8 | 1.6 | [10 empty] | Enabled |  |  | 1.018 | 1.018 | 1.528 | 1.528 | 2.7 | 2.7 | 0 | 0.8 | 1.6
PHT.116 | 116 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #1 | AREVA | MICOM P545 | 3379381/07/10 | NUMERIK | 2012 |  |  |  | 0 | 0 | 0.315 | 0.315 | 2.329 | 2.329 | 0 | 0.4 | 1.6 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.117 | 117 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#2 | #2 | 3000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #2 | AREVA | MICOM P545 | 3379382/05/09 | NUMERIK | 2011 |  |  |  | 0 | 0 | 0.315 | 0.315 | 2.329 | 2.329 | 0 | 0.4 | 1.6 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.118 | 118 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV TANGERANG #1 | SIEMENS | 7SL87 | BM1911005993 | NUMERIK | 2021 |  |  |  | 0.949 | 0.949 | 1.424 | 1.424 | 2.041 | 2.041 | 0 | 0.4 | 1.6 | [13 empty] | 0.949 | 0.949 | 1.424 | 1.424 | 2.041 | 2.041 | 0 | 0.4 | 1.6
PHT.119 | 119 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV CENGKARENG | PHT 150kV TANGERANG #2 | SIEMENS | 7SL87 | BM1911005990 | NUMERIK | 2021 |  |  |  | 0.949 | 0.949 | 1.424 | 1.424 | 2.041 | 2.041 | 0 | 0.4 | 1.6 | [13 empty] | 0.949 | 0.949 | 1.424 | 1.424 | 2.041 | 2.041 | 0 | 0.4 | 1.6
PHT.120 | 120 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#1 | #1 | 1000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #1 | Siemens | 7SL87 |  | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.121 | 121 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#2 | #2 | 1000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #2 | Siemens | 7SL87 |  | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.122 | 122 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #1 | ALSTOM | MICOM P545 | 33980376/02/17 | NUMERIK | 2018 |  |  |  | 0.264 | 0.264 | 7.944 | 7.944 | 15.661 | 15.661 | 0 | 0.4 | 1.6 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.123 | 123 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#2 | #2 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #2 | ALSTOM | MICOM P545 | 33980375/02/17 | NUMERIK | 2018 |  |  |  | 0.264 | 0.264 | 7.944 | 7.944 | 15.661 | 15.661 | 0 | 0.4 | 1.6 | [10 empty] | Disabled |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.124 | 124 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV ITS | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV ITS | ALSTOM | MICOM P545 | 33980378/02/17 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 5.51 | 5.51 | 8.26 | 8.26 | 13.82 | 13.82 | 0 | 0.4 | 1.6
PHT.125 | 125 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 | 4000/1 | 150 kV/100 V | MPU | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU | ALSTOM | MICOM P545 | 33980371/02/17 | NUMERIK | 2018 |  |  |  | 1.729 | 1.729 | 3.786 | 3.786 | 6.451 | 6.451 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 8.8 | 8.8 | 19.08 | 19.08 | 32.48 | 32.48 | 0 | 0.4 | 1.6
PHT.126 | 126 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#1 | #1 | 3000/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #1 | ALSTOM | MICOM P543 | 32069227/02/12 | NUMERIK | 2015 |  |  |  | 0.333 | 0.333 | 1.117 | 1.117 | 1.969 | 1.969 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.33 | 0.33 | 1.12 | 1.12 | 1.97 | 1.97 | 0 | 0.4 | 1.6
PHT.127 | 127 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #2 | ALSTOM | MICOM P545 | 34665003/12/18 | NUMERIK | 2020 |  |  |  | 0.222 | 0.222 | 0.745 | 0.745 | 1.313 | 1.313 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.35 | 0.35 | 0.88 | 0.88 | 1.2 | 1.2 | 0 | 0.4 | 1.6
PHT.128 | 128 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#1 | #1 | 3200/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV METLAND #1 | ALSTOM | MICOM P545 | 34486736/06/18 | NUMERIK | 2019 |  |  |  | 5.524 | 5.524 | 8.285 | 8.285 | 11.774 | 11.774 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 5.519 | 5.519 | 8.291 | 8.291 | 11.77 | 11.77 | 0 | 0.4 | 1.6
PHT.129 | 129 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GI 150KV CILEDUG | PHT 150kV METLAND #2 | ALSTOM | MICOM P545 | 34721257/02/19 | NUMERIK | 2019 |  |  |  | 3.452 | 3.452 | 5.178 | 5.178 | 7.359 | 7.359 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 3.449 | 3.449 | 5.18 | 5.18 | 7.36 | 7.36 | 0 | 0.4 | 1.6
PHT.130 | 130 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #1 | GE | MICOM P545 | 36039279/03/22 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 1.018 | 1.018 | 1.528 | 1.528 | 2.966 | 2.966 | 0 | 0.4 | 1.6
PHT.131 | 131 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #2 | GE | MICOM P545 | 36039282/03/22 | NUMERIK |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Enabled |  |  | 1.018 | 1.018 | 1.528 | 1.528 | 2.966 | 2.966 | 0 | 0.4 | 1.6
PHT.132 | 132 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV LMK | #1 | 1000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV LMK | ALSTOM | MICOM P443 | 34486778/06/18 | NUMERIK | 2019 |  |  |  | 0.01 | 0.01 | 1.41 | 1.41 | 2.25 | 2.25 | 0 | 0.8 | 1.2 | [10 empty] | Enabled |  |  | 0.01 | 0.01 | 1.41 | 1.41 | 2.25 | 2.25 | 0 | 0.8 | 1.2
PHT.133 | 133 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#1 | #1 | 1600/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #1 | SIEMENS | 7SL87 | BM1809009344 | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0.31 | 0.31 | 0.465 | 0.465 | 0.609 | 0.609 | 0 | 0.4 | 1.6
PHT.134 | 134 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#2 | #2 | 1600/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #2 | SIEMENS | 7SL87 | BM1909000272 | NUMERIK | 2020 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0.31 | 0.31 | 0.465 | 0.465 | 0.669 | 0.669 | 0 | 0.4 | 1.6
PHT.135 | 135 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#1 | #1 | 4000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #1 | ALSTOM | MICOM P545 | 34483353/06/18 | NUMERIK | 2019 |  |  |  | 0.5 | 0.5 | 0.787 | 0.787 | 1.289 | 1.289 | 0 | 0.4 | 1.6 | [10 empty] | DISABLED |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.136 | 136 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #2 | ALSTOM | MICOM P545 | 34482260/06/18 | NUMERIK | 2019 |  |  |  | 0.25 | 0.25 | 0.42 | 0.42 | 0.71 | 0.71 | 0 | 0.4 | 1.6 | [10 empty] | DISABLED |  |  | 0.25 | 0.25 | 0.42 | 0.42 | 0.71 | 0.71 | 0 | 0 | 0
PHT.137 | 137 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #1 | ALSTOM | MICOM P545 | 33081355/10/14 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | DISABLED |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.138 | 138 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #2 | ALSTOM | MICOM P546 | 33081360/10/14 | NUMERIK | 2018 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | DISABLED |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.139 | 139 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#1 | #1 | 3000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #1 | ABB | RED670 | T1645095 | NUMERIK | 2020 |  |  |  | 2.073 | 2.073 | 5.706 | 5.706 | 9.921 | 9.921 | 0 | 0.4 | 1.6 | [10 empty] | On |  |  | 2.07 | 2.07 | 5.71 | 5.71 | 9.92 | 9.92 | 0 | 0.4 | 1.6
PHT.140 | 140 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#2 | #2 | 4000/5 | 150 kV/100 V | MPU | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #2 | ABB | RED670 | T1645094 | NUMERIK | 2020 |  |  |  | 2.073 | 2.073 | 5.706 | 5.706 | 9.921 | 9.921 | 0 | 0.4 | 1.6 | [10 empty] | On |  |  | 2.07 | 2.07 | 5.71 | 5.71 | 9.92 | 9.92 | 0 | 0.4 | 1.6
PHT.141 | 141 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV CENGKARENG #1 | SIEMENS | 7SL87 | BM1911005996 | NUMERIK | 2021 |  |  |  | 0.949 | 0.949 | 1.424 | 1.424 | 2.943 | 2.943 | 0 | 0.8 | 1.6 | [13 empty] | 0.949 | 0.949 | 1.424 | 1.424 | 2.943 | 2.943 | 0 | 0.8 | 1.6
PHT.142 | 142 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV CENGKARENG #2 | SIEMENS | 7SL87 | BM1911005987 | NUMERIK | 2021 |  |  |  | 0.949 | 0.949 | 1.424 | 1.424 | 2.943 | 2.943 | 0 | 0.8 | 1.6 | [13 empty] | 0.949 | 0.949 | 1.424 | 1.424 | 2.493 | 2.493 | 0 | 0.8 | 1.6
PHT.143 | 143 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #1 | NR | PCS-931 | NRJB20155119B0560 | NUMERIK | 2021 |  |  |  | 0.415 | 0.415 | 0.623 | 0.623 | 0.943 | 0.943 | 0 | 0.4 | 1.6 | [13 empty] | 0.415 | 0.415 | 0.623 | 0.623 | 0.943 | 0.943 | 0 | 0.4 | 1.6
PHT.144 | 144 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #2 | NR | PCS-931 | NRJB20155119B0570 | NUMERIK | 2021 |  |  |  | 0.415 | 0.415 | 0.623 | 0.623 | 0.943 | 0.943 | 0 | 0.4 | 1.6 | [13 empty] | 0.415 | 0.415 | 0.623 | 0.623 | 0.943 | 0.943 | 0 | 0.4 | 1.6
PHT.145 | 145 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#1 | #1 | 4000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #1 | ALSTOM | MICOM P543 | 32069229/02/12 | NUMERIK | 2014 |  |  |  | 0.222 | 0.222 | 0.755 | 0.755 | 1.332 | 1.332 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 0.44 | 0.44 | 1.51 | 1.51 | 2.66 | 2.66 | 0 | 0.4 | 1.2
PHT.146 | 146 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #2 | ALSTOM | MICOM P545 | 34486819/06/18 | NUMERIK | 2020 |  |  |  | 0.222 | 0.222 | 0.755 | 0.755 | 1.332 | 1.332 | 0 | 0.4 | 1.2 | [10 empty] | Enabled |  |  | 0.35 | 0.35 | 0.89 | 0.89 | 1.53 | 1.53 | 0 | 0.4 | 1.2
PHT.147 | 147 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #1 | ABB | RED670 | T1809136 | NUMERIK | 2019 |  |  |  | 0.875 | 0.875 | 1.358 | 1.358 | 3.223 | 3.223 | 0 | 0.4 | 1.6 | [13 empty] | 0.88 | 0.88 | 1.36 | 1.36 | 3.22 | 3.22 | 0 | 0.4 | 1.6
PHT.148 | 148 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #2 | ABB | RED670 | T1809137 | NUMERIK | 2019 |  |  |  | 0.875 | 0.875 | 1.358 | 1.358 | 3.223 | 3.223 | 0 | 0.4 | 1.6 | [13 empty] | 0.88 | 0.88 | 1.36 | 1.36 | 3.22 | 3.22 | 0 | 0.4 | 1.6
PHT.149 | 149 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#1 | #1 | 3200/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV METLAND #1 | SIEMENS | 7SL87 | BM1802009731 | NUMERIK | 2019 |  |  |  | 0.256 | 0.256 | 1.117 | 1.117 | 1.999 | 1.999 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.150 | 150 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#2 | #2 | 3200/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV METLAND #2 | SIEMENS | 7SL87 | BM1801000462 | NUMERIK | 2019 |  |  |  | 0.256 | 0.256 | 1.117 | 1.117 | 1.999 | 1.999 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.151 | 151 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #1 | ALSTOM | MICOM P545 | 33081356/10/14 | NUMERIK | 2018 |  |  |  | 0.084 | 0.084 | 0.126 | 0.126 | 0.711 | 0.711 | 0 | 0.8 | 1.6 | [10 empty] | DISABLED |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.152 | 152 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #2 | ALSTOM | MICOM P546 | 33081359/10/14 | NUMERIK | 2018 |  |  |  | 0.084 | 0.084 | 0.126 | 0.126 | 0.711 | 0.711 | 0 | 0.8 | 1.6 | [10 empty] | DISABLED |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.153 | 153 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#1 | #1 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #1 | GE | MICOM P546 |  | NUMERIK | 2025 |  |  |  | 0.12 | 0.12 | 0.18 | 0.18 | 0.33 | 0.33 | 0 | 0.4 | 1.6 | [10 empty] | N/A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.154 | 154 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#2 | #2 | 1000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #2 | GE | MICOM P546 |  | NUMERIK | 2025 |  |  |  | 0.12 | 0.12 | 0.18 | 0.18 | 0.33 | 0.33 | 0 | 0.4 | 1.6 | [10 empty] | N/A |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.155 | 155 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#1 | #1 | 2000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #1 | NR | PCS-931 |  | NUMERIK | 2019 |  |  |  | 0.474 | 0.474 | 0.711 | 0.711 | 1.384 | 1.384 | 0 | 0.4 | 1.6 | [13 empty] | 0.474 | 0.474 | 0.711 | 0.711 | 1.384 | 1.384 | 0 | 0.4 | 1.6
PHT.156 | 156 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#2 | #2 | 2000/5 | 150 kV/100 V | MPU | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #2 | NR | PCS-931 |  | NUMERIK | 2019 |  |  |  | 0.474 | 0.474 | 0.711 | 0.711 | 1.384 | 1.384 | 0 | 0.4 | 1.6 | [13 empty] | 0.474 | 0.474 | 0.711 | 0.711 | 1.384 | 1.384 | 0 | 0.4 | 1.6
PHT.157 | 157 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV KEMBANGAN #1 | SIEMENS | 7SL87 | BM1802009734 | NUMERIK | 2022 |  |  |  | 0.799 | 0.799 | 1.439 | 1.439 | 2.953 | 2.953 | 0 | 0.8 | 1.6 | [13 empty] | 0.799 | 0.799 | 1.439 | 1.439 | 2.953 | 2.953 | 0 | 0.8 | 1.6
PHT.158 | 158 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV KEMBANGAN #2 | SIEMENS | 7SL87 | BM1801000459 | NUMERIK | 2022 |  |  |  | 0.799 | 0.799 | 1.439 | 1.439 | 2.953 | 2.953 | 0 | 0.8 | 1.6 | [13 empty] | 0.799 | 0.799 | 1.439 | 1.439 | 2.953 | 2.953 | 0 | 0.8 | 1.6
PHT.159 | 159 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV CILEDUG #1 | ALSTOM | MICOM P545 | 34486820/06/18 | NUMERIK | 2022 |  |  |  | 3.452 | 3.452 | 5.178 | 5.178 | 5.512 | 5.512 | 0 | 0.8 | 1.6 | [10 empty] | Enabled |  |  | 3.452 | 3.452 | 5.178 | 5.178 | 5.512 | 5.512 | 0 | 0.8 | 1.6
PHT.160 | 160 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV METLAND | PHT 150kV CILEDUG #2 | ALSTOM | MICOM P545 | 34486817 | NUMERIK | 2022 |  |  |  | 3.452 | 3.452 | 5.178 | 5.178 | 5.512 | 5.512 | 0 | 0.8 | 1.6 | [10 empty] | Enabled |  |  | 3.452 | 3.452 | 5.178 | 5.178 | 5.512 | 5.512 | 0 | 0.8 | 1.6
PHT.161 | 161 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #1 | ABB | RED670 | T1809138 | NUMERIK | 2019 |  |  |  | 0.875 | 0.875 | 1.312 | 1.312 | 8.051 | 8.051 | 0 | 0.4 | 1.6 | [13 empty] | 0.88 | 0.88 | 1.31 | 1.31 | 8.05 | 8.05 | 0 | 0.4 | 1.6
PHT.162 | 162 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #2 | ABB | RED670 | T1809135 | NUMERIK | 2019 |  |  |  | 0.875 | 0.875 | 1.312 | 1.312 | 8.051 | 8.051 | 0 | 0.4 | 1.6 | [13 empty] | 0.875 | 0.875 | 1.31 | 1.31 | 8.05 | 8.05 | 0 | 0.4 | 1.6
PHT.163 | 163 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#1 | #1 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #1 | ALSTOM | MICOM P545 | 34486822/06/18 | NUMERIK | 2019 |  |  |  | 0.452 | 0.452 | 1.886 | 1.886 | 6.253 | 6.253 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.45 | 0.45 | 1.88 | 1.88 | 6.25 | 6.25 | 0 | 0.4 | 1.6
PHT.164 | 164 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#2 | #2 | 2000/1 | 150 kV/100 V | MPU | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #2 | ALSTOM | MICOM P545 | 34486818/06/18 | NUMERIK | 2019 |  |  |  | 0.452 | 0.452 | 1.886 | 1.886 | 6.253 | 6.253 | 0 | 0.4 | 1.6 | [10 empty] | Enabled |  |  | 0.45 | 0.45 | 1.89 | 1.89 | 6.25 | 6.25 | 0 | 0.4 | 1.6
PHT.165 | 165 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | TOSHIBA | GRL 200 | VNT0682FM0001-1 | NUMERIK | 2020 |  |  |  | 6.143 | 6.199 | 9.215 | 9.179 | 14.75 | 25.9 | 0 | 0.8 | 1.2 | [13 empty] | 6.14 | 6.19 | 9.21 | 9.17 | 14.75 | 25.9 | 0 | 0.8 | 1.2
PHT.166 | 166 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | TOSHIBA | GRL 200 | VNT0682FM0001-2 | NUMERIK | 2020 |  |  |  | 0.704 | 0.702 | 5.055 | 5.036 | 9.215 | 25.9 | 0 | 0.4 | 1.6 | [13 empty] | 0.75 | 0.74 | 5.1 | 5.08 | 9.28 | 23.3 | 0 | 0.4 | 1.6
PHT.167 | 167 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | ABB | RED670 | T2136181 | NUMERIK |  |  |  |  | 2.139 | 2.139 | 2.709 | 2.709 | 4.276 | 4.276 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.168 | 168 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | ABB | RED670 | T2136163 | NUMERIK |  |  |  |  | 2.139 | 2.139 | 2.709 | 2.709 | 4.276 | 4.276 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.169 | 169 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | NR | PCS-931 | NRJB20155116B0350 | NUMERIK | 2020 |  |  |  | 6.143 | 6.143 | 9.215 | 9.215 | 14.75 | 14.75 | 0 | 0.8 | 1.2 | [13 empty] | 6.143 | 6.143 | 9.215 | 9.215 | 14.75 | 14.75 | 0 | 0.8 | 1.2
PHT.170 | 170 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | SIEMENS | 7SL87 | BM1801010766 | NUMERIK | 2020 |  |  |  | 0.702 | 0.702 | 5.036 | 5.036 | 9.179 | 9.179 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.171 | 171 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | SIEMENS | 7SL87 | BM2110007778 | NUMERIK |  |  |  |  | 1.711 | 1.711 | 2.567 | 2.567 | 3.421 | 3.421 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.172 | 172 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | SIEMENS | 7SL87 | BM2110007773 | NUMERIK |  |  |  |  | 1.711 | 1.711 | 2.567 | 2.567 | 3.421 | 3.421 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.173 | 173 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | TOSHIBA | GRL 200 | VNT0605FM0001-1 | NUMERIK |  |  |  |  | 0.696 | 0.693 | 2.292 | 2.2838 | 10.258 | 32.9 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.174 | 174 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | TOSHIBA | GRL 200 | VNT0605FM0001-2 | NUMERIK | 2020 |  |  |  | 0.696 | 0.693 | 2.292 | 2.2838 | 10.258 | 32.9 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.175 | 175 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | SIEMENS | 7SL87 | BM1801010778 | NUMERIK | 2022 |  |  |  | 0.702 | 0.702 | 5.036 | 5.036 | 9.179 | 9.179 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.176 | 176 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 4000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | SIEMENS | 7SL87 | BM1801010762 | NUMERIK | 2022 |  |  |  | 0.702 | 0.702 | 5.036 | 5.036 | 9.179 | 9.179 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.177 | 177 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 2000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | TOSHIBA | GRL 200 | VNT0773FM0001-1 | NUMERIK | 2019 |  |  |  | 2.721 | 2.709 | 4.074 | 4.063 | 13.279 | 10.998 | 0 | 0.4 | 1.6 | [13 empty] | 2.72 | 2.7 | 4.07 | 4.06 | 13.27 | 10.99 | 0 | 0.4 | 1.6
PHT.178 | 178 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 2000/1 | 500 kV/100 V | MPU-A | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | TOSHIBA | GRL 200 | VNT0773FM0001-2 | NUMERIK | 2019 |  |  |  | 2.721 | 2.709 | 4.074 | 4.063 | 13.279 | 10.998 | 0 | 0.4 | 1.6 | [13 empty] | 2.72 | 2.7 | 4.07 | 4.06 | 13.27 | 10.99 | 0 | 0.4 | 1.6
PHT.179 | 179 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | SIEMENS | 7SL87 | BM1801010448 | NUMERIK |  |  |  |  | 0.693 | 0.693 | 2.284 | 2.284 | 10.218 | 10.218 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.180 | 180 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | SIEMENS | 7SL87 | BM1801010453 | NUMERIK | 2020 |  |  |  | 0.693 | 0.693 | 2.284 | 2.284 | 10.218 | 10.218 | 0 | 0.4 | 1.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PHT.181 | 181 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | TOSHIBA | GRL 200 | VNT0682 FM 001-3 | NUMERIK | 2022 |  |  |  | 6.743 | 6.728 | 11.04 | 10.922 | 27.32 | 25.9 | 0 | 0.4 | 1.6 | [13 empty] | 7.95 | 7.93 | 12.24 | 12.13 | 29.12 | 37.39 | 0 | 0.4 | 1.6
PHT.182 | 182 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 4000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | TOSHIBA | GRL 200 | VNT0682 FM 001-6 | NUMERIK | 2022 |  |  |  | 6.743 | 6.728 | 11.04 | 10.922 | 27.32 | 25.9 | 0 | 0.4 | 1.6 | [13 empty] | 7.95 | 7.93 | 12.24 | 12.13 | 29.12 | 37.39 | 0 | 0.4 | 1.6
PHT.183 | 183 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 2000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | NR | PCS-931 | NRJB20155116B0340[FE4878] | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 2.719 | 2.719 | 4.079 | 4.079 | 13.275 | 13.275 | 0 | 0.4 | 1.6
PHT.184 | 184 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 2000/1 | 500 kV/100 V | MPU-B | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | NR | PCS-931 | NRJB2015516B0310[EF4AA8] | NUMERIK | 2019 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 2.719 | 2.719 | 4.079 | 4.079 | 13.275 | 13.275 | 0 | 0.4 | 1.6

## OCR_PHT
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | SIRKIT | RATIO CT - BPU | HELPER ASET |  | MERK | TYPE | NO. SERI | JENIS RELE | TH OPERASI | OCR | [9 empty] | OCR
[7 empty] | GI/GIS | BAY | [5 empty] | TAP SET | SETTING (TAP SETTING TERAKHIR) | [8 empty] | SET RELAY | SETTING (TERPASANG)
[15 empty] | In | Iset OC | tms OC | char OC | Iset GF | tms GF | char GF | PDF | TGL |  | In | Iset OC | tms OC | char OC | Iset GF | tms GF | char GF | TGL | FILE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 10 | 11 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32
PHT.01 | 1 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#1 | #1 | 2000/5 | GI 150KV ANGKE | PHT 150kV ANCOL #1 | ALSTOM | MICOM P142 | 34421639/04/18 | NUMERIK | 2019 |  | 5 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 5 | 5.15 | 0.42 | SI | 0.85 | 0.685 | SI
PHT.02 | 2 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#2 | #2 | 2000/5 | GI 150KV ANGKE | PHT 150kV ANCOL #2 | ALSTOM | MICOM P142 | 34421640/04/18 | NUMERIK | 2019 |  | 5 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 5 | 5.15 | 0.42 | SI | 0.85 | 0.685 | SI
PHT.03 | 3 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#1 | #1 | 4000/5 | GI 150KV ANGKE | PHT 150kV KARET LAMA #1 | GE | MICOM P142 | 34421644/04/18 | NUMERIK | 2019 |  | 5 | 3.75 | 0.373 | SI | 0.625 | 0.659 | SI | 6. Micom P142_Angke bay Karet lama 1,2.pdf | 2022-01-20 |  | 5 | 3.75 | 0.375 | SI | 0.65 | 0.66 | SI
PHT.04 | 4 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#2 | #2 | 4000/5 | GI 150KV ANGKE | PHT 150kV KARET LAMA #2 | GE | MICOM P142 | 34421643/04/18 | NUMERIK | 2019 |  | 5 | 3.75 | 0.373 | SI | 0.625 | 0.659 | SI | 6. Micom P142_Angke bay Karet lama 1,2.pdf | 2022-01-20 |  | 5 | 3.75 | 0.375 | SI | 0.65 | 0.66 | SI
PHT.05 | 5 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#1 | #1 | 2000/5 | GI 150KV ANGKE | PHT 150kV KETAPANG #1 | ALSTOM | MICOM P142 | 34421637/04/18 | NUMERIK | 2019 |  | 5 | 6 | 0.608 | SI | 1 | 0.879 | SI | Tap Setting Official Angke-Ketapang dan arah sebaliknya.pdf | 2019-03-06 |  | 5 | 7.5 | 0.58 | SI | 0.25 | 0.905 | SI
PHT.06 | 6 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#2 | #2 | 2000/5 | GI 150KV ANGKE | PHT 150kV KETAPANG #2 | ALSTOM | MICOM P142 | 34421638/04/18 | NUMERIK | 2021 |  | 5 | 6 | 0.608 | SI | 1 | 0.879 | SI | Tap Setting Official Angke-Ketapang dan arah sebaliknya.pdf | 2019-03-06 |  | 5 | 3.5 | 0.735 | SI | 0.25 | 0.905 | SI
PHT.07 | 7 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#1 | #1 | 4000/5 | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #1 | ALSTOM | MICOM P142 | 34421641/04/18 | NUMERIK | 2020 |  | 5 | 3.6 | 0.527 | SI | 0.6 | 0.846 | SI |  | 2026-01-14 |  | 5 | 3.6 | 0.48 | SI | 0.6 | 0.75 | SI
PHT.08 | 8 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#2 | #2 | 4000/5 | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #2 | ALSTOM | MICOM P142 | 34421642/04/18 | NUMERIK | 2020 |  | 5 | 3.6 | 0.48 | SI | 0.6 | 0.75 | SI |  | 2026-01-14 |  | 5 | 3.6 | 0.48 | SI | 0.6 | 0.75 | SI
PHT.09 | 9 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#1 | #1 | 2000/5 | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #1 | SIEMENS | 7SJ82 | BM1712006310 | NUMERIK | 2018 |  | 5 | 5.25 | 0.43 | SI | 0.875 | 0.522 | SI | Tap Setting Official ANGKE-MKLMA.pdf | 2018-07-12 |  | 5 | 5.25 | 0.43 | SI | 0.88 | 0.52 | SI
PHT.10 | 10 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#2 | #2 | 2000/5 | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #2 | SIEMENS | 7SJ82 | BM1712006313 | NUMERIK | 2018 |  | 5 | 5.25 | 0.43 | SI | 0.875 | 0.522 | SI | Tap Setting Official ANGKE-MKLMA.pdf | 2018-07-12 |  | 5 | 0 | 0 | SI | 0 | 0 | SI
PHT.11 | 11 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#1 | #1 | 4000/1 | GID 150KV DADAP | PHT 150kV LONTAR #1 | GE | MICOM P841 | 34465147/05/18 | NUMERIK | 2021 |  | 1 | 0.819 | 0.269 | SI | 0.137 | 0.531 | SI | 20200220_Dadap - Lontar 1_2.pdf | 2020-02-20 |  | 1 | 0.82 | 0.295 | SI | 0.14 | 0.6 | SI
PHT.12 | 12 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#2 | #2 | 4000/1 | GID 150KV DADAP | PHT 150kV LONTAR #2 | GE | MICOM P841 | 34465146/05/18 | NUMERIK | 2021 |  | 1 | 0.819 | 0.269 | SI | 0.137 | 0.531 | SI | 20200220_Dadap - Lontar 1_2.pdf | 2020-02-20 |  | 1 | 0.82 | 0.295 | SI | 0.14 | 0.6 | SI
PHT.13 | 13 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#1 | #1 | 4000/1 | GID 150KV DADAP | PHT 150kV TELUK NAGA #1 | GE | MICOM P841 | 34465150/05/18 | NUMERIK | 2021 |  | 1 | 0.819 | 0.269 | SI | 0.137 | 0.531 | SI | 20200220_Dadap - Teluk Naga 1_2.pdf | 2020-02-20 |  | 1 | 0.82 | 0.295 | SI | 0.14 | 0.6 | SI
PHT.14 | 14 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#2 | #2 | 4000/1 | GID 150KV DADAP | PHT 150kV TELUK NAGA #2 | GE | MICOM P841 | 34465148/05/18 | NUMERIK | 2021 |  | 1 | 0.819 | 0.269 | SI | 0.137 | 0.531 | SI | 20200220_Dadap - Teluk Naga 1_2.pdf | 2020-02-20 |  | 1 | 0.82 | 0.295 | SI | 0.14 | 0.6 | SI
PHT.15 | 15 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 2500/5 | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #1 | NR | PCS 9611S | NRJB2145332510102 | NUMERIK | 2025 |  | 5 | 4.8 | 0.469 | SI | 0.8 | 0.808 | SI | GI MUARAKARANG BARU BAY GIS MUARAKARANG BARU 1 & 2.pdf | 2025-09-20 |  | 5 | 4.8 | 0.469 | SI | 0.8 | 0.808 | SI
PHT.16 | 16 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 2500/5 | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #2 | NR | PCS 9611S | NRJB2145332510101 | NUMERIK | 2025 |  | 5 | 4.8 | 0.469 | SI | 0.8 | 0.808 | SI | GI MUARAKARANG BARU BAY GIS MUARAKARANG BARU 1 & 2.pdf | 2025-09-20 |  | 5 | 4.8 | 0.469 | SI | 0.8 | 0.808 | SI
PHT.17 | 17 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#1 | #1 | 4000/5 | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #1 | AREVA | MICOM P521 |  | NUMERIK |  |  | 5 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 5 | 2.55 | 0.65 | SI | 0 | 0 | SI
PHT.18 | 18 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#2 | #2 | 4000/5 | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #2 | ALSTOM | MICOM P543 |  | NUMERIK |  |  | 5 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 5 | 2.55 | 0.65 | SI | 0 | 0 | SI
PHT.19 | 19 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#1 | #1 | 2000/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #1 | SIEMENS | 7SJ82 | BFO807114017 | NUMERIK |  |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI | 20250623 - Tap Setting OCR GFR MKRLM - ANGKE 1,2 - signed.pdf | 2025-06-23 |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI
PHT.20 | 20 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#2 | #2 | 2000/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #2 | SIEMENS | 7SJ82 | BFO807114016 | NUMERIK |  |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI | 20250623 - Tap Setting OCR GFR MKRLM - ANGKE 1,2 - signed.pdf | 2025-06-23 |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI
PHT.21 | 21 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#1 | #1 | 1200/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #1 | SIEMENS | 7SJ62 | BFO807111344 | NUMERIK |  |  | 5 | 3.675 | 0.628 | SI | 0.615 | 0.975 | SI | 20250623 - Tap Setting OCR GFR MKRLM - BDKMY 1,2 - signed.pdf | 2025-06-23 |  | 5 | 3.675 | 0.628 | SI | 0.615 | 0.975 | SI
PHT.22 | 22 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#2 | #2 | 1200/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #2 | SIEMENS | 7SJ62 | BFO807114015 | NUMERIK |  |  | 5 | 3.675 | 0.628 | SI | 0.615 | 0.975 | SI | 20250623 - Tap Setting OCR GFR MKRLM - BDKMY 1,2 - signed.pdf | 2025-06-23 |  | 5 | 3.675 | 0.628 | SI | 0.615 | 0.975 | SI
PHT.23 | 23 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#1 | #1 | 2000/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #1 | AREVA | MICOM P521 |  | NUMERIK |  |  | 5 | 5 | 0.541 | SI | 0.835 | 0.804 | SI |  |  |  | 5 | 5 | 0.541 | SI | 0.835 | 0.804 | SI
PHT.24 | 24 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#2 | #2 | 2000/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #2 | ALSTOM | MICOM P543 |  | NUMERIK |  |  | 5 | 5 | 0.541 | SI | 0.835 | 0.804 | SI |  |  |  | 5 | 5 | 0.541 | SI | 0.835 | 0.804 | SI
PHT.25 | 25 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#1 | #1 | 2000/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #1 | SIEMENS | 7SJ62 | BM1712006311 | NUMERIK | 2018 |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI | Tap Setting Official MKLMA-ANGKE.pdf | 2018-07-12 |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI
PHT.26 | 26 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#2 | #2 | 2000/5 | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #2 | SIEMENS | 7SJ62 | BM1712006312 | NUMERIK | 2018 |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI | Tap Setting Official MKLMA-ANGKE.pdf | 2018-07-12 |  | 5 | 5.25 | 0.45 | SI | 0.875 | 0.79 | SI
PHT.27 | 27 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#1 | #1 | 3000/1 | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #1 | ABB | REF615 | IVHR91309441 | NUMERIK | 2019 |  | 1 | 1.006 | 0.335 | SI | 0.168 | 0.619 | SI | official tap setting proteksi sutt daan mogot - durikosambi 1,2_rev01.pdf | 2019-08-28 |  | 1 | 1.01 | 0.34 | SI | 0.168 | 0.619 | SI
PHT.28 | 28 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#2 | #2 | 3000/1 | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #2 | ABB | REF615 | IVHR91309444 | NUMERIK | 2019 |  | 1 | 1.006 | 0.335 | SI | 0.168 | 0.619 | SI | official tap setting proteksi sutt daan mogot - durikosambi 1,2_rev01.pdf | 2019-08-28 |  | 1 | 1.01 | 0.34 | SI | 0.17 | 0.62 | SI
PHT.29 | 29 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 3000/1 | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #1 | ABB | REF615 | IVHR91309442 | NUMERIK | 2019 |  | 1 | 1.006 | 0.335 | SI | 0.168 | 0.619 | SI | official tap setting proteksi sutt daan mogot - pik 1,2.pdf | 2019-07-31 |  | 1 | 1.01 | 0.34 | SI | 0.17 | 0.64 | SI
PHT.30 | 30 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 3000/1 | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #2 | ABB | REF615 | IVHR91309439 | NUMERIK | 2019 |  | 1 | 1.006 | 0.335 | SI | 0.168 | 0.619 | SI | official tap setting proteksi sutt daan mogot - pik 1,2.pdf | 2019-07-31 |  | 1 | 1.01 | 0.34 | SI | 0.17 | 0.64 | SI
PHT.31 | 31 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#1 | #1 | 1600/1 | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #1 | SCHNEIDER | MICOM P142 | 39732206/03/20 | NUMERIK | 2022 |  | 1 | 1.2 | 0.29 | SI | 0.2 | 0.586 | SI |  | 2026-01-14 |  | 1 | 1.2 | 0.35 | SI | 0.2 | 0.6 | SI
PHT.32 | 32 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#2 | #2 | 1600/1 | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #2 | SCHNEIDER | MICOM P142 | 39732187/03/20 | NUMERIK | 2022 |  | 1 | 1.2 | 0.42 | SI | 0.2 | 0.68 | SI |  | 2026-01-14 |  | 1 | 1.2 | 0.35 | SI | 0.2 | 0.6 | SI
PHT.33 | 33 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#1 | #1 | 2000/1 | GIS 150KV GROGOL | PHT 150kV TOMANG #1 | SIEMENS | 7SJ82 | BM1907004048 | NUMERIK | 2021 |  | 1 | 0.715 | 0.4 | SI | 0.12 | 0.674 | SI | official tap setting LCD, DIST, OCR grogol - tomang 1,2.pdf | 2019-10-31 |  | 1 | 0.72 | 0.36 | SI | 0.12 | 0.66 | SI
PHT.34 | 34 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#2 | #2 | 2000/1 | GIS 150KV GROGOL | PHT 150kV TOMANG #2 | SIEMENS | 7SJ82 | BM1907004722 | NUMERIK | 2021 |  | 1 | 0.715 | 0.4 | SI | 0.12 | 0.674 | SI | official tap setting LCD, DIST, OCR grogol - tomang 1,2.pdf | 2019-10-31 |  | 1 | 0.72 | 0.36 | SI | 0.12 | 0.66 | SI
PHT.35 | 35 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#1 | #1 | 2000/1 | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #1 | SIEMENS | 7SJ82 | BM1804004008 | NUMERIK | 2019 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI | Official Grogol II - Durikosambi.pdf | 2019-10-23 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI
PHT.36 | 36 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#2 | #2 | 2000/1 | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #2 | SIEMENS | 7SJ82 | BM1809003787 | NUMERIK | 2020 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI | Official Grogol II - Durikosambi.pdf | 2019-10-23 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI
PHT.37 | 37 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#1 | #1 | 2000/1 | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #1 | SIEMENS | 7SJ82 | BM1809003788 | NUMERIK | 2019 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI | Official Grogol II - Grogol.pdf | 2019-10-23 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI
PHT.38 | 38 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#2 | #2 | 2000/1 | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #2 | SIEMENS | 7SJ82 | BM1804004009 | NUMERIK | 2020 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI | Official Grogol II - Grogol.pdf | 2019-10-23 |  | 1 | 0.97 | 0.44 | SI | 0.16 | 0.71 | SI
PHT.39 | 39 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#1 | #1 | 1000/5 | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #1 | ABB | REF615 | 1VHR91331926 | NUMERIK | 2021 |  | 5 | 4.8 | 0.49 | SI | 0.8 | 0.75 | SI | 2021 10 22 - Rev02.Tap Setting GIS Kebon Jeruk bay Durikosambi 1,2.pdf | 2021-10-22 |  | 5 | 4.75 | 0.49 | SI | 0.8 | 0.75 | SI
PHT.40 | 40 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#2 | #2 | 1000/5 | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #2 | ABB | REF615 | 1VHR91327607 | NUMERIK |  |  | 5 | 5.52 | 0.459 | SI | 0.92 | 0.739 | SI | DAFTAR SETELAN RELAI PROTEKSI GIS 150kV KEBONJERUK_07.04.26.pdf | 2026-04-07 |  | 5 | 5.52 | 0.459 | SI | 0.92 | 0.739 | SI
PHT.41 | 41 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#1 | #1 | 500/5 | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #1 | ABB | REF615 | 1VHR91419341 | NUMERIK | 2021 |  | 5 | 4.3 | 0.615 | SI | 0.725 | 0.875 | SI | 21 10 22 - Rev02.Tap Setting GIS Kebon Jeruk bay Karet 2.pdf | 2021-10-22 |  | 5 | 6 | 0.56 | SI | 1 | 0.85 | SI
PHT.42 | 42 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#2 | #2 | 500/5 | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #2 | ABB | REF615 | 1VHR91419337 | NUMERIK | 2021 |  | 5 | 4.3 | 0.615 | SI | 0.725 | 0.875 | SI | 21 10 22 - Rev02.Tap Setting GIS Kebon Jeruk bay Karet 2.pdf | 2021-10-22 |  | 5 | 6 | 0.56 | SI | 1 | 0.85 | SI
PHT.43 | 43 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#1 | #1 | 2000/1 | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #1 | ALSTOM | MICOM P142 | 34724739/02/19 | NUMERIK | 2022 |  | 1 | 1.2 | 0.41 | SI | 0.2 | 0.74 | SI | Copy of UGC GIS Muarakarang Baru - Mkarang Baru (AIS) Sirkit 1_LCD P545_OCR P142_rev01.pdf | 2021-10-01 |  | 1 | 1.2 | 0.41 | SI | 0.2 | 0.74 | SI
PHT.44 | 44 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#2 | #2 | 2000/1 | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #2 | ALSTOM | MICOM P142 | 34724738/02/19 | NUMERIK | 2022 |  | 1 | 1.2 | 0.41 | SI | 0.2 | 0.74 | SI | Copy of UGC GIS Muarakarang Baru - Mkarang Baru (AIS) Sirkit 2_LCD P545_OCR P142_rev01.pdf | 2021-09-01 |  | 1 | 1.2 | 0.41 | SI | 0.2 | 0.74 | SI
PHT.45 | 45 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 4000/1 | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #1 | ALSTOM | MICOM P142 | 34724737/02/19 | NUMERIK | 2022 |  | 1 | 0.754 | 0.375 | SI | 0.126 | 0.704 | SI | GIS MUARAKARANG BARU BAY PIK 1,2.PDF | 2022-04-13 |  | 1 | 0.75 | 0.375 | SI | 0.13 | 0.705 | SI
PHT.46 | 46 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 4000/1 | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #2 | ALSTOM | MICOM P142 | 34724836/02/19 | NUMERIK | 2022 |  | 1 | 0.754 | 0.375 | SI | 0.126 | 0.704 | SI | GIS MUARAKARANG BARU BAY PIK 1,2.PDF | 2022-04-13 |  | 1 | 0.75 | 0.375 | SI | 0.13 | 0.705 | SI
PHT.47 | 47 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#1 | #1 | 1000/5 | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #1 | SCHNEIDER | MICOM P123 | 36265213/12/13 | NUMERIK | 2021 |  | 5 | 5.55 | 0.447 | SI | 0.925 | 0.76 | SI |  | 2026-01-21 |  | 5 | 5.55 | 0.4 | SI | 0.9 | 0.725 | SI
PHT.48 | 48 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#2 | #2 | 1000/5 | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #2 | SCHNEIDER | MICOM P123 | 36265220/12/13 | NUMERIK | 2021 |  | 5 | 5.55 | 0.447 | SI | 0.925 | 0.76 | SI |  | 2026-01-21 |  | 5 | 5.55 | 0.4 | SI | 0.9 | 0.725 | SI
PHT.49 | 49 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#1 | #1 | 2000/1 | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #1 | ALSTOM | MICOM 14DL | 33493500/11/15 | NUMERIK | 2019 |  | 1 | 0.55 | 0.47 | SI | 0.1 | 0.75 | SI | Rev.01 OCGF_P14D NewSenayan - Senayan (1).pdf | 2020-11-12 |  | 1 | 0.66 | 0.5 | SI | 0.11 | 0.78 | SI
PHT.50 | 50 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#2 | #2 | 2000/1 | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #2 | ALSTOM | MICOM 14DL | 33493501/11/15 | NUMERIK | 2019 |  | 1 | 0.55 | 0.47 | SI | 0.1 | 0.75 | SI | Rev.01 OCGF_P14D NewSenayan - Senayan (1).pdf | 2020-11-12 |  | 1 | 0.55 | 0.47 | SI | 0.1 | 0.77 | SI
PHT.51 | 51 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#1 | #1 | 2000/1 | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #1 | NR | PCS-9611 | NRJB2088871832020 | NUMERIK | 2021 |  | 1 | 0.442 | 0.45 | SI | 0.074 | 0.747 | SI | 151. LCD_PCS931_PCS9611_New Senayan - Senayan Baru II #1.pdf | 2020-11-13 |  | 1 | 0.44 | 0.45 | SI | 0.074 | 0.747 | SI
PHT.52 | 52 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#2 | #2 | 2000/1 | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #2 | NR | PCS-9611 | NRJB2088871831460 | NUMERIK | 2021 |  | 1 | 0.442 | 0.45 | SI | 0.074 | 0.747 | SI | 151. LCD_PCS931_PCS9611_New Senayan - Senayan Baru II #1.pdf | 2020-11-13 |  | 1 | 0.44 | 0.45 | SI | 0.074 | 0.747 | SI
PHT.53 | 53 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#1 | #1 | 4000/1 | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #1 | SIEMENS | 7SJ63 | BF1205071875 | NUMERIK | 2016 |  | 1 | 0.754 | 0.33 | SI | 0.126 | 0.626 | SI | official tap setting proteksi sutt pik - daan mogot 1,2.pdf | 2019-07-31 |  | 1 | 0.753 | 0.33 | SI | 0.1352 | 0.63 | SI
PHT.54 | 54 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#2 | #2 | 4000/1 | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #2 | SIEMENS | 7SJ63 | BF1205071874 | NUMERIK | 2016 |  | 1 | 0.754 | 0.33 | SI | 0.126 | 0.626 | SI | official tap setting proteksi sutt pik - daan mogot 1,2.pdf | 2019-07-31 |  | 1 | 0.75 | 0.33 | SI | 0.13 | 0.63 | SI
PHT.55 | 55 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 4000/1 | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #1 | SIEMENS | 7SJ63 | BF1205071873 | NUMERIK | 2016 |  | 1 | 0.75 | 0.345 | SI | 0.13 | 0.63 | SI | 2021 03 24 - Tap Setting GIS Pantai Indah Kapuk Bay Muarakarang Baru #1,2.pdf | 2021-03-24 |  | 1 | 0.75 | 0.31 | SI | 0.13 | 0.57 | SI
PHT.56 | 56 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 4000/1 | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #2 | SIEMENS | 7SJ63 | BF1205071872 | NUMERIK | 2016 |  | 1 | 0.75 | 0.345 | SI | 0.13 | 0.63 | SI | 2021 03 24 - Tap Setting GIS Pantai Indah Kapuk Bay Muarakarang Baru #1,2.pdf | 2021-03-24 |  | 1 | 0.75 | 0.31 | SI | 0.12 | 0.57 | SI
PHT.57 | 57 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#1 | #1 | 2000/1 | GIS 150KV TOMANG | PHT 150kV GROGOL #1 | ALSTOM | MICOM P142 | 37070223/05/19 | NUMERIK | 2021 |  | 1 | 0.715 | 0.4 | SI | 0.12 | 0.674 | SI | official tap setting LCD, DIST, OCR tomang - grogol 1,2.pdf | 2019-10-31 |  | 1 | 0.72 | 0.4 | SI | 0.12 | 0.675 | SI
PHT.58 | 58 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#2 | #2 | 2000/1 | GIS 150KV TOMANG | PHT 150kV GROGOL #2 | ALSTOM | MICOM P142 | 39634244/11/17 | NUMERIK | 2021 |  | 1 | 0.715 | 0.4 | SI | 0.12 | 0.674 | SI | official tap setting LCD, DIST, OCR tomang - grogol 1,2.pdf | 2019-10-31 |  | 1 | 0.72 | 0.4 | SI | 0.12 | 0.675 | SI
PHT.59 | 59 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#1 | #1 | 2000/1 | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #1 | GE | MICOM P14D | 34731620/03/19 | NUMERIK | 2021 |  | 1 | 0.442 | 0.45 | SI | 0.074 | 0.747 | SI | 20210401_ULUJAMI_NEW SENAYAN_2.pdf | 2021-04-03 |  | 1 | 0.44 | 0.45 | SI | 0.07 | 0.745 | SI
PHT.60 | 60 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#2 | #2 | 2000/1 | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #2 | GE | MICOM P14D | 34731617/03/19 | NUMERIK | 2021 |  | 1 | 0.442 | 0.45 | SI | 0.074 | 0.747 | SI | 20210401_ULUJAMI_NEW SENAYAN_2.pdf | 2021-04-03 |  | 1 | 0.44 | 0.45 | SI | 0.07 | 0.745 | SI
PHT.61 | 61 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.62 | 62 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.63 | 63 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.64 | 64 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.65 | 65 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | [7 empty] | 0 | 0 | SI | 0 | 0 | SI |  |  |  |  | 0 | 0 | SI | 0 | 0 | SI
PHT.66 | 66 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | [7 empty] | 0 | 0 | SI | 0 | 0 | SI |  |  |  |  | 0 | 0 | SI | 0 | 0 | SI
PHT.67 | 67 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1 | [7 empty] | 0 | 0 | SI | 0 | 0 | SI |  |  |  |  | 0 | 0 | SI | 0 | 0 | SI
PHT.68 | 68 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 |  | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2 | [7 empty] | 0 | 0 | SI | 0 | 0 | SI |  |  |  |  | 0 | 0 | SI | 0 | 0 | SI
PHT.69 | 69 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#1 | #1 | 2000/1 | GI 150KV CURUG | PHT 150kV CIKUPA #1 | ALSTOM | MICOM P14D | 34721250/02/19 | NUMERIK | 2019 |  | 1 | 0.85 | 0.387 | SI | 0.14 | 0.663 | SI | 2021 01 22 - Tap Setting GI Curug Bay Cikupa #1.pdf | 2021-01-22 |  | 1 | 0.85 | 0.39 | SI | 0.14 | 0.66 | SI
PHT.70 | 70 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#2 | #2 | 3200/1 | GI 150KV CURUG | PHT 150kV CIKUPA #2 | GE | MICOM P14D | 36535238/10/23 | NUMERIK | 2010 |  | 1 | 0.531 | 0.3934 | SI | 0.0885 | 0.6755 | SI | OCR PHT curug - cikupa #2 (1).pdf | 2024-09-10 |  | 1 | 0.53 | 0.425 | SI | 0.09 | 0.7 | SI
PHT.71 | 71 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 3200/1 | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #1 | GE | MICOM P14D | 36537697/10/23 | NUMERIK | 2010 |  | 1 | 0.542 | 0.3904 | SI | 0.091 | 0.6723 | SI | OCR PHT CURUG - SUMMARECON GADING SERPONG #1 (1).pdf | 2019-08-12 |  | 1 | 0.54 | 0.4 | SI | 0.093 | 0.675 | SI
PHT.72 | 72 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 2000/1 | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #2 | ALSTOM | MICOM P14D | 34721249/02/19 | NUMERIK | 2019 |  | 1 | 0.87 | 0.41 | SI | 0.144 | 0.685 | SI | 2021 11 16 - Tap Setting GI Curug Bay Summarecon #2.pdf | 2019-08-12 |  | 1 | 0.87 | 0.41 | SI | 0.14 | 0.685 | SI
PHT.73 | 73 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | #1 | 2000/1 | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | ABB | REF 615 | 1VHR91312363 | NUMERIK | 2021 |  | 1 |  |  | SI |  |  | SI | 20171123_Tap Setting Gajah Tunggal - Pasar Kemis 1_2.pdf | 2017-11-23 |  | 1 |  |  | SI |  |  | SI
PHT.74 | 74 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | #1 | 2000/1 | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | ABB | REF 615 | 1VHR91312359 | NUMERIK | 2021 |  | 1 | 0.97 | 0.34 | SI | 0.16 | 0.61 | SI | 20171123_Tap Setting Gajah Tunggal - Sepatan 1_2.pdf | 2017-11-23 |  | 1 | 0.97 | 0.35 | SI | 0.16 | 0.64 | SI
PHT.75 | 75 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV TANGERANG BARU | #1 | 4000/1 | GI 150KV ITS | PHT 150kV TANGERANG BARU | SIEMENS | 7SJ82 | BM2102004948 | NUMERIK | 2021 |  | 1 | 1.124 | 0.212 | SI | 0.187 | 0.473 | SI | 132. [signed] KTT ITS Bay Tangerang Baru.pdf | 2021-07-29 |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.76 | 76 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV CENGKARENG BARU | #1 | 4000/1 | GI 150KV ITS | PHT 150kV CENGKARENG BARU | SIEMENS | 7SS85 | BM2102007389 | NUMERIK | 2021 |  | 1 | 0.95 | 0.234 | SI | 0.158 | 0.486 | SI | 133. [signed] KTT ITS Bay Cengkareng Baru.pdf | 2021-07-29 |  | 1 | 0.95 | 0.234 | SI | 0.158 | 0.486 | SI
PHT.77 | 77 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV KONSUMEN | #1 | 300/1 | GI 150KV ITS | PHT 150kV KONSUMEN | SIEMENS | 7SJ82 | BM2102004944 | NUMERIK | 2021 |  | 1 | 1.2 | 0.628 | SI | 0.2 | 0.901 | SI | 135. [signed] GI ITS Bay Consumer.pdf | 2021-07-29 |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.78 | 78 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#1 | #1 | 1600/5 | GI 150KV JATAKE | PHT 150kV CIKUPA #1 | ABB | REF615 | 1VHR91419670 | NUMERIK | 2019 |  | 5 | 4.675 | 0.36 | SI | 0.78 | 0.62 | SI | 20250928_Tap Setting_OCR_GFR GI Jatake bay Cikupa 1 - signed.pdf | 2025-09-28 |  | 5 | 4.675 | 0.36 | SI | 0.78 | 0.62 | SI
PHT.79 | 79 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#2 | #2 | 1600/5 | GI 150KV JATAKE | PHT 150kV CIKUPA #2 | SCHNEIDER | MICOM P142 | 39731744/04/20 | NUMERIK | 2021 |  | 5 | 6 | 0.375 | SI | 1 | 0.635 | SI | 2023 10 28 - Tap Setting GI Jatake bay Cikupa #2.pdf | 2023-10-28 |  | 5 | 6 | 0.375 | SI | 1 | 0.635 | SI
PHT.80 | 80 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#1 | #1 | 1600/5 | GI 150KV JATAKE | PHT 150kV JATAKE BARU #1 | SCHNEIDER | MICOM P122 | 36188977/01/13 | NUMERIK |  |  | 5 | 6 | 0.394 | SI | 1 | 0.66 | SI | GI Jatake Lama bay Jatake II 1,2_OCR Revisi (1).pdf | 2020-07-28 |  | 5 | 6 | 0.394 | SI | 1 | 0.66 | SI
PHT.81 | 81 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#2 | #2 | 1600/5 | GI 150KV JATAKE | PHT 150kV JATAKE BARU #2 | SCHNEIDER | MICOM P123 | 36189409/02/13 | NUMERIK |  |  | 5 | 6 | 0.394 | SI | 1 | 0.66 | SI | GI Jatake Lama bay Jatake II 1,2_OCR Revisi (1).pdf | 2020-07-28 |  | 5 | 4.85 | 0.354 | SI | 0.825 | 0.609 | SI
PHT.82 | 82 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 1000/1 | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | NR | PCS-9611 | NRJB2088871830060 | NUMERIK | 2019 |  | 1 | 1.2 | 0.405 | SI | 0.2 | 0.669 | SI | Jatake-Maxi (1).pdf | 2018-08-30 |  | 1 | 1.2 | 0.427 | SI | 0.184 | 0.7 | SI
PHT.83 | 83 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 1000/1 | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | NR | PCS-9611 | NRJB2088871830070 | NUMERIK | 2019 |  | 1 | 1.2 | 0.405 | SI | 0.2 | 0.669 | SI | Jatake-Maxi (1).pdf | 2018-08-30 |  | 1 | 1.2 | 0.405 | SI | 0.2 | 0.669 | SI
PHT.84 | 84 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 1000/1 | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | [6 empty] | 1 | 1.2 | 0.405 | SI | 0.2 | 0.669 | SI |  |  |  | 1 | 1.2 | 0.427 | SI | 0.184 | 0.7 | SI
PHT.85 | 85 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 1000/1 | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | [6 empty] | 1 | 1.2 | 0.405 | SI | 0.2 | 0.669 | SI |  |  |  | 1 | 1.2 | 0.405 | SI | 0.2 | 0.669 | SI
PHT.86 | 86 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 1000/1 | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | NR | PCS-9611 | NRJB2088871830960 | NUMERIK | 2019 |  | 1 | 1.2 | 0.402 | SI | 0.2 | 0.665 | SI | Maxi-Jatake (1).pdf | 2018-08-30 |  | 1 | 1.2 | 0.123 | SI | 0.184 | 0.69 | SI
PHT.87 | 87 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 1000/1 | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | NR | PCS-9611 | NRJB2088871830970 | NUMERIK | 2020 |  | 1 | 1.2 | 0.402 | SI | 0.2 | 0.665 | SI | Maxi-Jatake (1).pdf | 2018-08-30 |  | 1 | 1.1 | 0.436 | SI | 0.184 | 0.69 | SI
PHT.88 | 88 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 1000/1 | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | [6 empty] | 1 | 1.2 | 0.402 | SI | 0.2 | 0.665 | SI |  |  |  | 1 | 1.2 | 0.123 | SI | 0.184 | 0.69 | SI
PHT.89 | 89 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 1000/1 | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | [6 empty] | 1 | 1.2 | 0.402 | SI | 0.2 | 0.665 | SI |  |  |  | 1 | 1.1 | 0.436 | SI | 0.184 | 0.69 | SI
PHT.90 | 90 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#1 | #1 | 4000/1 | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #1 | NR | PCS-9611 |  | NUMERIK | 2021 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI | PCS931_TBII-Balaraja.pdf | 2020-05-13 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI
PHT.91 | 91 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#2 | #2 | 4000/1 | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #2 | NR | PCS-9611 |  | NUMERIK | 2021 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI | PCS931_TBII-Balaraja.pdf | 2020-05-13 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI
PHT.92 | 92 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#1 | #1 | 4000/1 | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #1 | NR | PCS-9611 |  | NUMERIK | 2021 |  | 1 | 0.82 | 0.374 | SI | 0.137 | 0.65 | SI | tap setting DIST_OCR_PCS931_PCS9611_OHL Tangerang Baru II - Lontar 1,2_rev02 (AR by Selector Switch).pdf | 2020-11-07 |  | 1 | 0.82 | 0.374 | SI | 0.137 | 0.65 | SI
PHT.93 | 93 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#2 | #2 | 4000/1 | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #2 | NR | PCS-9611 |  | NUMERIK | 2021 |  | 1 | 0.82 | 0.374 | SI | 0.137 | 0.65 | SI | tap setting DIST_OCR_PCS931_PCS9611_OHL Tangerang Baru II - Lontar 1,2_rev02 (AR by Selector Switch).pdf | 2020-11-07 |  | 1 | 0.82 | 0.374 | SI | 0.137 | 0.65 | SI
PHT.94 | 94 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#1 | #1 | 4000/1 | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #1 | NR | PCS-9611 |  | NUMERIK | 2021 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI | PCS931_TBII-Suvarna.pdf | 2020-05-13 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI
PHT.95 | 95 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#2 | #2 | 4000/1 | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #2 | NR | PCS-9611 |  | NUMERIK | 2021 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI | PCS931_TBII-Suvarna.pdf | 2020-05-13 |  | 1 | 0.819 | 0.359 | SI | 0.137 | 0.625 | SI
PHT.96 | 96 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#1 | #1 | 3000/1 | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #1 | AREVA | MICOM P141 | 3375740/05/10 | NUMERIK |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 1.09 | 0.3 | SI | 0.18 | 0.56 | SI
PHT.97 | 97 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#2 | #2 | 3000/1 | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #2 | AREVA | MICOM P141 | 3171263/05/08 | NUMERIK |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 1.09 | 0.3 | SI | 0.18 | 0.56 | SI
PHT.98 | 98 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV ITS | #1 | 3000/1 | GI 150KV TANGERANG BARU | PHT 150kV ITS | AREVA | MICOM P141 | 3377540/05/09 | NUMERIK |  |  | 1 | 1.2 | 0.222 | SI | 0.2 | 0.469 | SI | 2026 04 20 GI Tangerang Baru bay ITS_Resetting OCR.pdf | 2026-04-20 |  | 1 | 1.2 | 0.222 | SI | 0.2 | 0.469 | SI
PHT.99 | 99 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 | 3000/1 | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | AREVA | MICOM P141 | 3375742/03/09 | NUMERIK |  |  | 1 | 1.2 | 0.222 | SI | 0.2 | 0.469 | SI | DAFTAR SETELAN RELAI PROTEKSi Gl 150 kV CENGKARENG BARU_10.03.26.pdf | 2026-03-10 |  | 1 | 0.96 | 0.295 | SI | 0.24 | 0.5 | SI
PHT.100 | 100 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#1 | #1 | 3000/1 | GI 150KV TELUK NAGA | PHT 150kV DADAP #1 | AREVA | MICOM P141 | 3375737/03/09 | NUMERIK | 2023 |  | 1 | 1.092 | 0.269 | SI | 0.182 | 0.531 | SI | 20200219_Tap Setting Teluk Naga - Dadap 1&2.pdf | 2020-02-19 |  | 1 | 1.2 | 0.275 | SI | 0.2 | 0.525 | SI
PHT.101 | 101 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#2 | #2 | 3000/1 | GI 150KV TELUK NAGA | PHT 150kV DADAP #2 | AREVA | MICOM P141 | 3377538/05/09 | NUMERIK | 2022 |  | 1 | 1.092 | 0.269 | SI | 0.182 | 0.531 | SI | 20200219_Tap Setting Teluk Naga - Dadap 1&2.pdf | 2020-02-19 |  | 1 | 1.2 | 0.275 | SI | 0.2 | 0.525 | SI
PHT.102 | 102 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#1 | #1 | 1600/1 | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #1 | GE | MICOM P14D | 36173634/09/22 | NUMERIK |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI | 12. P14D_OCR_Teluk Naga bay Sepatan #1 (1).pdf | 2023-01-17 |  | 1 | 1.2 | 0.25 | SI | 0.2 | 0.45 | SI
PHT.103 | 103 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#2 | #2 | 1600/1 | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #2 | SCHNEIDER | MICOM P142 | 39732209/03/20 | NUMERIK |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 1.2 | 0.25 | SI | 0.2 | 0.45 | SI
PHT.104 | 104 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#1 | #1 | 2000/1 | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #1 | NR | PCS-9611 | NRJB21322819B0070 | NUMERIK | 2021 |  | 1 | 0.972 | 0.374 | SI | 0.162 | 0.636 | SI | GI Jatake II bay Jatake Lama ,12_PCS931 Revisi Final (1).pdf | 2021-02-01 |  | 1 | 0.972 | 0.374 | SI | 0.162 | 0.636 | SI
PHT.105 | 105 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#2 | #2 | 2000/1 | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #2 | NR | PCS-9611 | NRJB21322819B0080 | NUMERIK | 2021 |  | 1 | 0.972 | 0.374 | SI | 0.162 | 0.636 | SI | GI Jatake II bay Jatake Lama ,12_PCS931 Revisi Final (1).pdf | 2021-02-01 |  | 1 | 0.972 | 0.374 | SI | 0.162 | 0.636 | SI
PHT.106 | 106 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#1 | #1 | 2000/1 | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #1 | NR | PCS-9611 | NRJB21322819B0110 | NUMERIK | 2021 |  | 1 | 0.972 | 0.374 | SI | 0.162 | 0.636 | SI | GI Jatake II bay Tangerang Lama ,12_PCS931 Revisi Final.pdf | 2021-02-01 |  | 1 | 0.972 | 0.374 | SI | 0.164 | 0.636 | SI
PHT.107 | 107 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#2 | #2 | 2000/1 | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #2 | NR | PCS-9611 | NRJB21322819B0100 | NUMERIK | 2021 |  | 1 | 0.972 | 0.374 | SI | 0.162 | 0.636 | SI | GI Jatake II bay Tangerang Lama ,12_PCS931 Revisi Final.pdf | 2021-02-01 |  | 1 | 0.972 | 0.374 | SI | 0.164 | 0.636 | SI
PHT.108 | 108 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#1 | #1 | 4000/1 | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #1 | NR | RCS-9611 | 7728100900201 | NUMERIK |  |  | 1 | 0.82 | 0.346 | SI | 0.137 | 0.642 | SI | 20200220_LONTAR-DADAP 1_2.pdf | 2020-02-20 |  | 1 | 0.82 | 0.345 | SI | 0.14 | 0.64 | SI
PHT.109 | 109 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#2 | #2 | 4000/1 | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #2 | NR | RCS-9611 | 7728100900101 | NUMERIK |  |  | 1 | 0.82 | 0.346 | SI | 0.137 | 0.642 | SI | 20200220_LONTAR-DADAP 1_2.pdf | 2020-02-20 |  | 1 | 0.82 | 0.345 | SI | 0.14 | 0.64 | SI
PHT.110 | 110 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#1 | #1 | 3000/1 | GIS 150KV LONTAR | PHT 150kV DADAP #1 | SCHNEIDER | MICOM P142 | 39619258/07/17 | NUMERIK | 2021 |  | 1 | 1.092 | 0.304 | SI | 0.182 | 0.617 | SI | official tap setting DIST_OCR_schneider p443_p142_OHL Lontar - Tangerang Baru II 1,2_rev01.pdf | 2020-06-20 |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.111 | 111 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#2 | #2 | 3000/1 | GIS 150KV LONTAR | PHT 150kV DADAP #2 | SCHNEIDER | MICOM P142 | 39619259/07/17 | NUMERIK | 2021 |  | 1 | 1.092 | 0.304 | SI | 0.182 | 0.617 | SI | official tap setting DIST_OCR_schneider p443_p142_OHL Lontar - Tangerang Baru II 1,2_rev01.pdf | 2020-06-20 |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.112 | 112 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#1 | #1 | 3000/1 | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #1 | NR | PCS-9611S | NRJB2145332510118 | NUMERIK | 2026 |  | 1 | 1.059 | 0.362 | SI | 0.177 | 0.677 | SI | 107 GIS LONTAR BAY TANGERANG BARU 1-2_260612_155850.pdf | 2026-06-11 |  | 1 | 1.059 | 0.362 | SI | 0.177 | 0.677 | SI
PHT.113 | 113 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#2 | #2 | 3000/1 | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #2 | NR | RCS-9611 | 7728095200101 | NUMERIK |  |  | 1 | 1.09 | 0.33 | SI | 0.18 | 0.63 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.114 | 114 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#1 | #1 | 2000/5 | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #1 | AREVA | MICOM P141 | 3375744/05/09 | NUMERIK | 2012 |  | 5 | 4.8 | 0.34 | SI | 0.8 | 0.59 | SI | OCR Cengkareng lama bay ckrg 2.pdf | 2017-12-29 |  | 5 | 0 | 0 | SI | 0 | 0 | SI
PHT.115 | 115 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#2 | #2 | 2000/5 | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #2 | AREVA | MICOM P141 | 3375738/05/09 | NUMERIK | 2011 |  | 5 | 4.8 | 0.34 | SI | 0.8 | 0.59 | SI | 2022 05 12 - Tap Setting GI Cengkareng - Cengkareng Baru #2.pdf | 2022-05-12 |  | 5 | 4.8 | 0.34 | SI | 0.8 | 0.591 | SI
PHT.116 | 116 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#1 | #1 | 4000/5 | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #1 | SCHNEIDER | MICOM P122 | 36119231 | NUMERIK | 2014 |  | 5 | 61.2 | 0.242 | SI | 10.2 | 0.496 | SI |  |  |  | 5 | 4.75 | 0.23 | SI | 0.8 | 0.48 | SI
PHT.117 | 117 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#2 | #2 | 3000/5 | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #2 | SCHNEIDER | MICOM P122 | 31379982 | NUMERIK | 2010 |  | 5 | 61.2 | 0.242 | SI | 10.2 | 0.496 | SI | 2021 08 24 - Tap Setting GI Cengkareng bay Durikosambi 2.pdf | 2021-08-24 |  | 5 | 6 | 0.22 | SI | 1 | 0.47 | SI
PHT.118 | 118 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#1 | #1 | 2000/5 | GI 150KV CENGKARENG | PHT 150kV TANGERANG #1 | SIEMENS | 7SJ82 | BM1911002879 | NUMERIK | 2021 |  | 5 | 3.75 | 0.373 | SI | 0.625 | 0.632 | SI | MiComP122 CNKNG bay TGRNG 1,2 - 29 08 2019.pdf | 2019-08-30 |  | 5 | 3.75 | 0.38 | SI | 0.63 | 0.64 | SI
PHT.119 | 119 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#2 | #2 | 2000/5 | GI 150KV CENGKARENG | PHT 150kV TANGERANG #2 | SIEMENS | 7SJ82 | BM1911002878 | NUMERIK | 2021 |  | 5 | 3.75 | 0.373 | SI | 0.625 | 0.632 | SI | MiComP122 CNKNG bay TGRNG 1,2 - 29 08 2019.pdf | 2019-08-30 |  | 5 | 3.75 | 0.38 | SI | 0.63 | 0.64 | SI
PHT.120 | 120 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#1 | #1 | 1000/1 | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #1 | ALSTOM | MICOM P141 | 33980359/02/17 | NUMERIK | 2018 |  | 1 | 0.886 | 0.427 | SI | 0.148 | 0.686 | SI | rev 1 OCR BSH.pdf | 2019-02-28 |  | 1 | 0.89 | 0.43 | SI | 0.15 | 0.69 | SI
PHT.121 | 121 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#2 | #2 | 1000/1 | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #2 | ALSTOM | MICOM P141 | 33980358/02/17 | NUMERIK | 2018 |  | 1 | 0.886 | 0.427 | SI | 0.148 | 0.686 | SI | rev 1 OCR BSH.pdf | 2019-02-28 |  | 1 | 0.89 | 0.43 | SI | 0.15 | 0.69 | SI
PHT.122 | 122 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#1 | #1 | 4000/1 | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #1 | ALSTOM | MICOM P141 | 33980363/02/17 | NUMERIK | 2018 |  | 1 | 0.945 | 0.235 | SI | 0.158 | 0.487 | SI | 2022 05 11 - Tap Setting GI Cengkareng Baru - Cengkareng #1,2.pdf | 2022-05-12 |  | 1 | 0.95 | 0.21 | SI | 0.16 | 0.46 | SI
PHT.123 | 123 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#2 | #2 | 4000/1 | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #2 | ALSTOM | MICOM P14D | 33980360/02/17 | NUMERIK | 2019 |  | 1 | 0.945 | 0.235 | SI | 0.158 | 0.487 | SI | 2022 05 11 - Tap Setting GI Cengkareng Baru - Cengkareng #1,2.pdf | 2022-05-12 |  | 1 | 0.95 | 235 | SI | 0.16 | 485 | SI
PHT.124 | 124 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV ITS | #1 | 4000/1 | GI 150KV CENGKARENG BARU | PHT 150kV ITS | ALSTOM | MICOM P14D | 33980362/02/17 | NUMERIK | 2019 |  | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0.72 | 0.27 | SI | 0.12 | 0.52 | SI
PHT.125 | 125 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 | 4000/1 | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU | ALSTOM | MICOM P141 | 33980364/02/17 | NUMERIK | 2018 |  | 1 | 1.14 | 0.137 | SI | 0.19 | 0.371 | SI | DAFTAR SETELAN RELAI PROTEKSi Gl 150 kV CENGKARENG BARU_10.03.26.pdf | 2026-03-10 |  | 1 | 0.95 | 0.21 | SI | 0.16 | 0.46 | SI
PHT.126 | 126 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#1 | #1 | 3000/1 | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #1 | SCHNEIDER | MICOM P142 | 39732573/04/20 | NUMERIK | 2021 |  | 1 | 0.57 | 0.415 | SI | 0.095 | 0.715 | SI | 2021 03 23 - Tap Setting GI Ciledug Bay Alam Sutera #1 - Rev02.pdf | 2021-03-23 |  | 1 | 0.57 | 0.415 | SI | 0.1 | 0.715 | SI
PHT.127 | 127 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#2 | #2 | 2000/1 | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #2 | ALSTOM | MICOM P141 | 34104380/08/17 | NUMERIK | 2020 |  | 1 | 0.86 | 0.415 | SI | 0.145 | 0.71 | SI | 2022 03 10 - Tap Setting GI Ciledug bay Alam Sutera #2.pdf | 2022-03-10 |  | 1 | 0.86 | 0.415 | SI | 0.15 | 0.71 | SI
PHT.128 | 128 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#1 | #1 | 3200/1 | GI 150KV CILEDUG | PHT 150kV METLAND #1 | ALSTOM | MCGG 52 | 781860H | NUMERIK | 2001 |  | 1 | 0.517 | 0.42 | SI | 0.086 | 0.718 | SI | tap setting UGC Ciledug - Kembangan II 1_LCD DIST-P545_OCR-P142.pdf | 2022-03-03 |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.129 | 129 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#2 | #2 | 2000/1 | GI 150KV CILEDUG | PHT 150kV METLAND #2 | ALSTOM | MICOM P142 | 34721251/02/19 | NUMERIK | 2019 |  | 1 | 0.827 | 0.42 | SI | 0.138 | 0.718 | SI | tap setting UGC Ciledug - Kembangan II 2_LCD DIST-P545_OCR-P142.pdf | 2022-03-03 |  | 1 | 0.83 | 0.42 | SI | 0.14 | 0.72 | SI
PHT.130 | 130 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#1 | #1 | 2000/5 | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #1 | SCHNEIDER | MICOM P142 | 39732215/03/20 | NUMERIK | 2022 |  | 5 | 4.75 | 0.45 | SI | 0.75 | 0.8 | SI | 2021 03 25 - Tap Setting OCR GFR Penghantar GI Durikosambi - Cengkareng #1.pdf | 2021-03-25 |  | 5 | 4.75 | 0.45 | SI | 0.75 | 0.8 | SI
PHT.131 | 131 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#2 | #2 | 2000/5 | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #2 | SCHNEIDER | MICOM P142 | 39732216/03/20 | NUMERIK | 2022 |  | 5 | 4.75 | 0.45 | SI | 0.75 | 0.8 | SI | 2021 08 18 - Tap Setting OCR GFR Penghantar GI Durikosambi - Cengkareng #2.pdf | 2021-08-18 |  | 5 | 4.75 | 0.45 | SI | 0.75 | 0.8 | SI
PHT.132 | 132 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV LMK | #1 | 1000/5 | GI 150KV DURIKOSAMBI | PHT 150kV LMK | SCHNEIDER | MICOM P142 | 39733329/04/20 | NUMERIK | 2022 |  | 5 | 4.68 | 0.446 | SI | 0.78 | 0.774 | SI |  |  |  | 5 | 4.68 | 0.446 | SI | 0.78 | 0.774 | SI
PHT.133 | 133 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#1 | #1 | 1600/5 | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #1 | SCHNEIDER | MICOM P142 | 39732577/04/20 | NUMERIK | 2022 |  | 5 | 6 | 0.337 | SI | 1 | 0.666 | SI |  |  |  | 5 | 6 | 0.4 | SI | 1 | 0.55 | SI
PHT.134 | 134 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#2 | #2 | 1600/5 | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #2 | SCHNEIDER | MICOM P142 | 39733319/04/20 | NUMERIK | 2022 |  | 5 | 6 | 0.337 | SI | 1 | 0.666 | SI |  |  |  | 5 | 6 | 0.4 | SI | 1 | 0.55 | SI
PHT.135 | 135 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#1 | #1 | 4000/5 | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #1 | SCHNEIDER | MICOM P142 | 39733323/04/20 | NUMERIK | 2022 |  | 5 | 1.38 | 0.421 | SI | 0.23 | 0.748 | SI |  |  |  | 5 | 1.25 | 0.3 | SI | 0.4 | 0.3 | SI
PHT.136 | 136 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#2 | #2 | 2000/5 | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #2 | SCHNEIDER | MICOM P122 | 36013228 | NUMERIK |  |  | 5 | 2.76 | 0.421 | SI | 0.46 | 0.748 | SI | DAFTAR SETELAN RELAI PROTEKSI Gl 150kV DURIKOSAMBI_07.04.26.pdf | 2026-04-07 |  | 5 | 2.76 | 0.421 | SI | 0.46 | 0.748 | SI
PHT.137 | 137 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#1 | #1 | 1000/5 | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #1 | SCHNEIDER | MICOM P122 | 36013234 | NUMERIK |  |  | 5 | 5.52 | 0.421 | SI | 0.92 | 0.748 | SI |  |  |  | 5 | 4.75 | 0.525 | SI | 0.75 | 0.85 | SI
PHT.138 | 138 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#2 | #2 | 1000/5 | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #2 | SCHNEIDER | MICOM P142 | 39732202/03/20 | NUMERIK | 2022 |  | 5 | 5.52 | 0.421 | SI | 0.92 | 0.748 | SI |  |  |  | 5 | 4.75 | 0.525 | SI | 0.75 | 0.85 | SI
PHT.139 | 139 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#1 | #1 | 3000/5 | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #1 | SCHNEIDER | MICOM P142 | 39732214/03/20 | NUMERIK | 2022 |  | 5 | 5.03 | 0.358 | SI | 0.84 | 0.659 | SI | official tap setting proteksi sutt durikosambi - daan mogot 1_rev01.pdf | 2019-08-28 |  | 5 | 3.8 | 0.385 | SI | 0.65 | 0.775 | SI
PHT.140 | 140 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#2 | #2 | 4000/5 | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #2 | SCHNEIDER | MICOM P142 | 39732579/04/20 | NUMERIK | 2022 |  | 5 | 5.03 | 0.358 | SI | 0.84 | 0.659 | SI | official tap setting proteksi sutt durikosambi - daan mogot 2_rev01.pdf | 2019-08-28 |  | 5 | 3.8 | 0.35 | SI | 0.75 | 0.675 | SI
PHT.141 | 141 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#1 | #1 | 2000/5 | GI 150KV TANGERANG | PHT 150kV CENGKARENG #1 | SIEMENS | 7SJ82 | BM1911002877 | NUMERIK | 2021 |  | 5 | 3.75 | 0.385 | SI | 0.625 | 0.64 | SI | 2020 01 31 - Tap Setting GI Tangerang Lama bay Cengkareng 1,2.pdf | 2020-02-03 |  | 5 | 3.75 | 385 | SI | 0.63 | 0.64 | SI
PHT.142 | 142 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#2 | #2 | 2000/5 | GI 150KV TANGERANG | PHT 150kV CENGKARENG #2 | SIEMENS | 7SJ82 | BM1911002876 | NUMERIK | 2021 |  | 5 | 3.75 | 0.385 | SI | 0.625 | 0.64 | SI | 2020 01 31 - Tap Setting GI Tangerang Lama bay Cengkareng 1,2.pdf | 2020-02-03 |  | 5 | 3.75 | 0.38 | SI | 0.63 | 0.64 | SI
PHT.143 | 143 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#1 | #1 | 2000/5 | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #1 | SCHNEIDER | MICOM P122 | 36119230 | NUMERIK |  |  | 5 | 4.86 | 0.355 | SI | 0.81 | 0.61 | SI | GI Tangerang Lama bay Jatake II-1,2 PCS931 Revisi Final.pdf | 2021-02-01 |  | 5 | 4.85 | 0.355 | SI | 0.8 | 0.61 | SI
PHT.144 | 144 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#2 | #2 | 2000/5 | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #2 | SCHNEIDER | MICOM P122 | 36119266 | NUMERIK |  |  | 5 | 4.86 | 0.355 | SI | 0.81 | 0.61 | SI | GI Tangerang Lama bay Jatake II-1,2 PCS931 Revisi Final.pdf | 2021-02-01 |  | 5 | 4.86 | 0.355 | SI | 0.81 | 0.61 | SI
PHT.145 | 145 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#1 | #1 | 4000/1 | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #1 | ALSTOM | MICOM P141 | 32065265/02/12 | NUMERIK | 2014 |  | 1 | 0.86 | 0.415 | SI | 0.14 | 0.705 | SI | 2021 03 23 - Tap Setting GIS Alam Sutera Bay Ciledug #1 - Rev02.pdf | 2021-03-23 |  | 1 | 0.86 | 0.415 | SI | 0.14 | 0.705 | SI
PHT.146 | 146 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#2 | #2 | 2000/1 | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #2 | ALSTOM | MICOM P141 | 32065264/02/12 | NUMERIK | 2020 |  | 1 | 0.86 | 0.415 | SI | 0.145 | 0.7 | SI | 2021 03 23 - Tap Setting GIS Alam Sutera Bay Ciledug #2 - Rev02.pdf | 2021-03-23 |  | 1 | 0.86 | 0.415 | SI | 0.15 | 0.7 | SI
PHT.147 | 147 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 2000/1 | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #1 | ALSTOM | MICOM P141 | 32065267/02/12 | NUMERIK | 2019 |  | 1 | 0.96 | 0.73 | SI | 0.16 | 0.64 | SI | OCR Alsut-Summarecon.pdf | 2019-05-13 |  | 1 | 0.91 | 0.4 | SI | 0.15 | 0.695 | SI
PHT.148 | 148 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 2000/1 | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #2 | ALSTOM | MICOM P141 | 32065268/02/12 | NUMERIK | 2019 |  | 1 | 0.96 | 0.73 | SI | 0.16 | 0.64 | SI | OCR Alsut-Summarecon.pdf | 2019-05-13 |  | 1 | 0.91 | 0.4 | SI | 0.15 | 0.695 | SI
PHT.149 | 149 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#1 | #1 | 3200/5 | GIS 150KV KEMBANGAN | PHT 150kV METLAND #1 | SCHNEIDER | MICOM P142 | 39732572/04/20 | NUMERIK | 2022 |  | 5 | 2.584 | 0.428 | SI | 0.431 | 0.75 | SI | 2021 01 22 - Tap Setting GIS Kembangan Bay Durikosambi #1,2.Rev01.pdf | 2021-01-22 |  | 5 | 2.6 | 0.43 | SI | 0.45 | 0.75 | SI
PHT.150 | 150 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#2 | #2 | 3200/5 | GIS 150KV KEMBANGAN | PHT 150kV METLAND #2 | SCHNEIDER | MICOM P142 | 39732191/03/20 | NUMERIK | 2022 |  | 5 | 2.584 | 0.428 | SI | 0.431 | 0.75 | SI | 2021 01 22 - Tap Setting GIS Kembangan Bay Durikosambi #1,2.Rev01.pdf | 2021-01-22 |  | 5 | 2.6 | 0.425 | SI | 0.45 | 0.75 | SI
PHT.151 | 151 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#1 | #1 | 1000/5 | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #1 | SCHNEIDER | MICOM P142 | 39732574/04/20 | NUMERIK | 2022 |  | 5 | 4.75 | 0.475 | SI | 0.75 | 0.8 | SI | tap setting UGC Kembangan - Kembangan II _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-03-04 |  | 5 | 4.75 | 0.475 | SI | 0.75 | 0.8 | SI
PHT.152 | 152 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#2 | #2 | 1000/5 | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #2 | SCHNEIDER | MICOM P142 | 39732204/03/20 | NUMERIK | 2022 |  | 5 | 4.75 | 0.475 | SI | 0.75 | 0.8 | SI | tap setting UGC Kembangan - Kembangan II _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-03-04 |  | 5 | 4.75 | 0.475 | SI | 0.75 | 0.8 | SI
PHT.153 | 153 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#1 | #1 | 1000/5 | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #1 | AREVA | MICOM P123 | 30032469 | NUMERIK |  |  | 5 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 5 | 5.55 | 0.5 | SI | 0.925 | 0.825 | SI
PHT.154 | 154 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#2 | #2 | 1000/5 | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #2 | AREVA | MICOM P142 | 30032470 | NUMERIK |  |  | 5 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 5 | 5.55 | 0.5 | SI | 0.925 | 0.825 | SI
PHT.155 | 155 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#1 | #1 | 2000/5 | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #1 | ALSTOM | MICOM P141 | 33239251/03/15 | NUMERIK | 2019 |  | 5 | 6 | 0.44 | SI | 1 | 0.77 | SI | Tap Setting Kembangan - Petukangan P545.pdf | 2018-12-24 |  | 5 | 6 | 0.44 | SI | 1 | 0.77 | SI
PHT.156 | 156 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#2 | #2 | 2000/5 | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #2 | ALSTOM | MICOM P141 | 33239250/03/15 | NUMERIK | 2019 |  | 5 | 6 | 0.44 | SI | 1 | 0.77 | SI | Tap Setting Kembangan - Petukangan P545.pdf | 2018-12-24 |  | 5 | 6 | 0.44 | SI | 1 | 0.77 | SI
PHT.157 | 157 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#1 | #1 | 2000/1 | GIS 150KV METLAND | PHT 150kV KEMBANGAN #1 | SIEMENS | 7SJ82 | BM1711001314 | NUMERIK |  |  | 1 | 0.827 | 0.428 | SI | 0.1378 | 0.75 | SI | TAPSET~3.PDF | 2023-10-19 |  | 1 | 0.827 | 0.43 | SI | 0.138 | 0.75 | SI
PHT.158 | 158 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#2 | #2 | 2000/1 | GIS 150KV METLAND | PHT 150kV KEMBANGAN #2 | SIEMENS | 7SJ82 | BM1802000759 | NUMERIK |  |  | 1 | 0.827 | 0.428 | SI | 0.1378 | 0.75 | SI | TAPSET~3.PDF | 2023-10-19 |  | 1 | 0.827 | 0.43 | SI | 0.138 | 0.75 | SI
PHT.159 | 159 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#1 | #1 | 2000/1 | GIS 150KV METLAND | PHT 150kV CILEDUG #1 | SIEMENS | 7SJ82 | BM1802000762 | NUMERIK |  |  | 1 | 0.827 | 0.428 | SI | 0.138 | 0.75 | SI | tap setting UGC Kembangan II - Kembangan _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-06-30 |  | 1 | 0.87 | 0.43 | SI | 0.138 | 0.75 | SI
PHT.160 | 160 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#2 | #2 | 2000/1 | GIS 150KV METLAND | PHT 150kV CILEDUG #2 | SIEMENS | 7SJ82 | BM1802000758 | NUMERIK |  |  | 1 | 0.827 | 0.428 | SI | 0.138 | 0.75 | SI | tap setting UGC Kembangan II - Kembangan _LCD dist 7SL87_OCR 7SJ82.pdf | 2022-06-30 |  | 1 | 0.827 | 0.43 | SI | 0.138 | 0.75 | SI
PHT.161 | 161 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#1 | #1 | 2000/1 | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #1 | ABB | REF 615 | 1VHR91392166 | NUMERIK | 2019 |  | 1 | 0.96 | 0.37 | SI | 0.16 | 0.62 | SI | 20190513_SUMMARECON_ALAM SUTERA_1&2 (OCR).pdf | 2019-05-13 |  | 1 | 0.91 | 0.4 | SI | 0.15 | 0.69 | SI
PHT.162 | 162 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#2 | #2 | 2000/1 | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #2 | ABB | REF 615 | 1VHR91392162 | NUMERIK | 2019 |  | 1 | 0.96 | 0.37 | SI | 0.16 | 0.62 | SI | 20190513_SUMMARECON_ALAM SUTERA_1&2 (OCR).pdf | 2019-05-13 |  | 1 | 0.91 | 0.4 | SI | 0.15 | 0.69 | SI
PHT.163 | 163 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#1 | #1 | 2000/1 | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #1 | ABB | REF 615 | 1VHR91392164 | NUMERIK | 2019 |  | 1 | 1.07 | 0.37 | SI | 0.18 | 0.65 | SI | Summarecon-Curug.pdf | 2019-08-12 |  | 1 | 0.87 | 0.41 | SI | 0.145 | 0.7 | SI
PHT.164 | 164 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#2 | #2 | 2000/1 | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #2 | ABB | REF 615 | 1VHR91392163 | NUMERIK | 2019 |  | 1 | 1.07 | 0.37 | SI | 0.18 | 0.65 | SI | Summarecon-Curug.pdf | 2019-08-12 |  | 1 | 0.87 | 0.41 | SI | 0.145 | 0.7 | SI
PHT.165 | 165 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.166 | 166 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.167 | 167 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.168 | 168 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.169 | 169 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.170 | 170 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.171 | 171 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.172 | 172 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 4000/1 | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.173 | 173 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.174 | 174 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.175 | 175 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.176 | 176 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.177 | 177 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 2000/1 | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.178 | 178 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 2000/1 | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.179 | 179 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.180 | 180 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.181 | 181 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.182 | 182 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 4000/1 | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.183 | 183 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 2000/1 | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI
PHT.184 | 184 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 2000/1 | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2 | [6 empty] | 1 | 0 | 0 | SI | 0 | 0 | SI |  |  |  | 1 | 0 | 0 | SI | 0 | 0 | SI

## AR
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | SIRKIT | AR (EKSTERNAL/INTERNAL) | HELPER ASET |  | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | AR |  |  |  |  | AR
[7 empty] | GI/GIS | BAY | [5 empty] | TAP SET | SETTING |  |  |  | SET RELAY | SETTING
[15 empty] | Pole | Dead Time 1 Pole | Dead Time 3 Pole | Reclaim Time |  | Pole | Dead Time 1 Pole | Dead Time 3 Pole | Reclaim Time
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
PHT.01 | 1 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#1 | #1 | Internal | GI 150KV ANGKE | PHT 150kV ANCOL #1 | GEC Alsthom | MVTR01 | 604474C | Elektromekanik | 2001
PHT.02 | 2 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#2 | #2 | Internal | GI 150KV ANGKE | PHT 150kV ANCOL #2 | GEC Alsthom | MVTR01 | 604477C | Elektromekanik | 2001
PHT.03 | 3 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#1 | #1 | Internal | GI 150KV ANGKE | PHT 150kV KARET LAMA #1
PHT.04 | 4 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#2 | #2 | Internal | GI 150KV ANGKE | PHT 150kV KARET LAMA #2
PHT.05 | 5 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#1 | #1 | Tidak Aktif | GI 150KV ANGKE | PHT 150kV KETAPANG #1
PHT.06 | 6 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#2 | #2 | Tidak Aktif | GI 150KV ANGKE | PHT 150kV KETAPANG #2
PHT.07 | 7 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#1 | #1 | Tidak Aktif | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #1
PHT.08 | 8 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#2 | #2 | Tidak Aktif | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA #2
PHT.09 | 9 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#1 | #1 | Tidak Aktif | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #1
PHT.10 | 10 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#2 | #2 | Tidak Aktif | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA #2
PHT.11 | 11 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#1 | #1 | Internal | GID 150KV DADAP | PHT 150kV LONTAR #1
PHT.12 | 12 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#2 | #2 | Internal | GID 150KV DADAP | PHT 150kV LONTAR #2
PHT.13 | 13 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#1 | #1 | Internal | GID 150KV DADAP | PHT 150kV TELUK NAGA #1
PHT.14 | 14 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#2 | #2 | Internal | GID 150KV DADAP | PHT 150kV TELUK NAGA #2
PHT.15 | 15 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | Tidak Aktif | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #1
PHT.16 | 16 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | Tidak Aktif | GI 150KV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU #2
PHT.17 | 17 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#1 | #1 | Tidak Aktif | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #1
PHT.18 | 18 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#2 | #2 | Tidak Aktif | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA #2
PHT.19 | 19 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#1 | #1 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #1
PHT.20 | 20 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#2 | #2 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE #2
PHT.21 | 21 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#1 | #1 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #1
PHT.22 | 22 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#2 | #2 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN #2
PHT.23 | 23 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#1 | #1 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #1
PHT.24 | 24 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#2 | #2 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU #2
PHT.25 | 25 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#1 | #1 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #1
PHT.26 | 26 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#2 | #2 | Tidak Aktif | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE #2
PHT.27 | 27 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#1 | #1 | Internal | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #1
PHT.28 | 28 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#2 | #2 | Internal | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI #2
PHT.29 | 29 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | Internal | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #1
PHT.30 | 30 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | Internal | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK #2
PHT.31 | 31 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#1 | #1 | Eksternal | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #1 | Alsthom | LFAA 101 |  | Elektromekanik
PHT.32 | 32 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#2 | #2 | Eksternal | GIS 150KV GROGOL | PHT 150kV GROGOL BARU #2 | Alsthom | LFAA 101 |  | Elektromekanik
PHT.33 | 33 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#1 | #1 | Tidak Aktif | GIS 150KV GROGOL | PHT 150kV TOMANG #1
PHT.34 | 34 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#2 | #2 | Tidak Aktif | GIS 150KV GROGOL | PHT 150kV TOMANG #2
PHT.35 | 35 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#1 | #1 | Internal | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #1
PHT.36 | 36 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#2 | #2 | Internal | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI #2
PHT.37 | 37 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#1 | #1 | Internal | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #1
PHT.38 | 38 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#2 | #2 | Internal | GIS 150KV GROGOL BARU | PHT 150kV GROGOL #2
PHT.39 | 39 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#1 | #1 | Tidak Aktif | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #1
PHT.40 | 40 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#2 | #2 | Tidak Aktif | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI #2
PHT.41 | 41 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#1 | #1 | Tidak Aktif | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #1
PHT.42 | 42 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#2 | #2 | Tidak Aktif | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU #2
PHT.43 | 43 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#1 | #1 | Tidak Aktif | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #1
PHT.44 | 44 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#2 | #2 | Tidak Aktif | GIS 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU #2
PHT.45 | 45 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | Eksternal | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #1 | Schneider | MICOM P841 |  | Numerik
PHT.46 | 46 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | Eksternal | GIS 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK #2 | Schneider | MICOM P841 |  | Numerik
PHT.47 | 47 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#1 | #1 | Tidak Aktif | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #1
PHT.48 | 48 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#2 | #2 | Tidak Aktif | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN #2
PHT.49 | 49 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#1 | #1 | Tidak Aktif | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #1
PHT.50 | 50 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#2 | #2 | Tidak Aktif | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN #2
PHT.51 | 51 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#1 | #1 | Tidak Aktif | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #1
PHT.52 | 52 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#2 | #2 | Tidak Aktif | GIS 150KV NEW SENAYAN | PHT 150kV ULUJAMI #2
PHT.53 | 53 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#1 | #1 | Internal | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #1 | Alstom | MiCom P545 | 197931U | Numerik |  |  |  | 1 |  | 40
PHT.54 | 54 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#2 | #2 | Internal | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT #2
PHT.55 | 55 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | Internal | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #1
PHT.56 | 56 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | Internal | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU #2
PHT.57 | 57 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#1 | #1 | Tidak Aktif | GIS 150KV TOMANG | PHT 150kV GROGOL #1
PHT.58 | 58 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#2 | #2 | Tidak Aktif | GIS 150KV TOMANG | PHT 150kV GROGOL #2
PHT.59 | 59 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#1 | #1 | Tidak Aktif | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #1
PHT.60 | 60 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#2 | #2 | Tidak Aktif | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN #2
PHT.61 | 61 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1
PHT.62 | 62 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2
PHT.63 | 63 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #1
PHT.64 | 64 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI #2
PHT.65 | 65 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1
PHT.66 | 66 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2
PHT.67 | 67 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #1
PHT.68 | 68 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 | Eksternal | GISTET 500KV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK #2
PHT.69 | 69 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#1 | #1 | Tidak Aktif | GI 150KV CURUG | PHT 150kV CIKUPA #1
PHT.70 | 70 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#2 | #2 | Tidak Aktif | GI 150KV CURUG | PHT 150kV CIKUPA #2
PHT.71 | 71 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | Tidak Aktif | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #1
PHT.72 | 72 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | Tidak Aktif | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG #2
PHT.73 | 73 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | #1 |  | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS
PHT.74 | 74 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | #1 | Internal | GI 150KV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU
PHT.75 | 75 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV TANGERANG BARU | #1 | Internal | GI 150KV ITS | PHT 150kV TANGERANG BARU
PHT.76 | 76 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV CENGKARENG BARU | #1 | Internal | GI 150KV ITS | PHT 150kV CENGKARENG BARU
PHT.77 | 77 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV KONSUMEN | #1 | Tidak Aktif | GI 150KV ITS | PHT 150kV KONSUMEN
PHT.78 | 78 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#1 | #1 |  | GI 150KV JATAKE | PHT 150kV CIKUPA #1
PHT.79 | 79 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#2 | #2 |  | GI 150KV JATAKE | PHT 150kV CIKUPA #2
PHT.80 | 80 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#1 | #1 | Internal | GI 150KV JATAKE | PHT 150kV JATAKE BARU #1
PHT.81 | 81 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#2 | #2 | Internal | GI 150KV JATAKE | PHT 150kV JATAKE BARU #2
PHT.82 | 82 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | Tidak Aktif | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1 | Alstom | MiCom P442 | 31830604/07/11 | Numerik |  |  |  | 1 |  | 40
PHT.83 | 83 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | Tidak Aktif | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2 | Alstom | MiCom P442 | 31830509/07/11 | Numerik |  |  |  | 1 |  | 40
PHT.84 | 84 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | Tidak Aktif | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #1
PHT.85 | 85 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | Tidak Aktif | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO #2
PHT.86 | 86 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | Tidak Aktif | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 |  | 40
PHT.87 | 87 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | Tidak Aktif | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 |  | 40
PHT.88 | 88 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | Tidak Aktif | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #1
PHT.89 | 89 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | Tidak Aktif | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE #2
PHT.90 | 90 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#1 | #1 | Internal | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #1 | NR | PCS-931 |  | Numerik | 2021 |  |  | 0.9 |  | 40
PHT.91 | 91 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#2 | #2 | Internal | GI 150KV SINDANG JAYA | PHT 150kV BALARAJA #2 | NR | PCS-931 |  | Numerik | 2021 |  |  | 0.9 |  | 40
PHT.92 | 92 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#1 | #1 | Internal | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #1 | NR | PCS-931 |  | Numerik | 2021 |  |  | 0.9 |  | 40
PHT.93 | 93 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#2 | #2 | Internal | GI 150KV SINDANG JAYA | PHT 150kV LONTAR #2 | NR | PCS-931 |  | Numerik | 2021 |  |  | 0.9 |  | 40
PHT.94 | 94 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#1 | #1 | Internal | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #1 | [7 empty] | 0.9 |  | 40
PHT.95 | 95 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#2 | #2 | Internal | GI 150KV SINDANG JAYA | PHT 150kV SUVARNA SUTERA #2 | [7 empty] | 0.9 |  | 40
PHT.96 | 96 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#1 | #1 | Eksternal | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #1 | Areva | KAVR 13 |  | Elektromekanik
PHT.97 | 97 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#2 | #2 | Eksternal | GI 150KV TANGERANG BARU | PHT 150kV LONTAR #2 | Areva | KAVR 13 |  | Elektromekanik
PHT.98 | 98 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV ITS | #1 | Eksternal | GI 150KV TANGERANG BARU | PHT 150kV ITS | Areva | KAVR 13 | 3354779/02/09 | Elektromekanik |  |  |  | 0.5 |  | 40
PHT.99 | 99 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 | Eksternal | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | Areva | KAVR 13 | 3354778/02/09 | Elektromekanik |  |  |  | 0.35 |  | 40
PHT.100 | 100 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#1 | #1 | Eksternal | GI 150KV TELUK NAGA | PHT 150kV DADAP #1 | Areva | KAVR 13 | 3354784/02/09 | Elektromekanik |  |  |  | 4.55 |  | 10
PHT.101 | 101 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#2 | #2 | Eksternal | GI 150KV TELUK NAGA | PHT 150kV DADAP #2 | Areva | KAVR 13 | 3354775/02/09 | Elektromekanik |  |  |  | 4.55 |  | 10
PHT.102 | 102 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#1 | #1 | Internal | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #1 | Alsthom | LFAA 101 | 690036F | Elektromekanik |  |  |  | 1 |  | 40
PHT.103 | 103 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#2 | #2 | Internal | GI 150KV TELUK NAGA | PHT 150kV SEPATAN #2 | Alsthom | LFAA 101 | 690047F | Elektromekanik |  |  |  | 1 |  | 40
PHT.104 | 104 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#1 | #1 | Internal | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #1 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 s |  | 40 s
PHT.105 | 105 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#2 | #2 | Internal | GIS 150KV JATAKE BARU | PHT 150kV JATAKE #2 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 s |  | 40 s
PHT.106 | 106 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#1 | #1 | Internal | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #1 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 s |  | 40 s
PHT.107 | 107 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#2 | #2 | Internal | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG #2 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 s |  | 40 s
PHT.108 | 108 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#1 | #1 | Eksternal | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #1 | Schneider | MICOM P841 |  | Numerik | 2021
PHT.109 | 109 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#2 | #2 | Eksternal | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA #2 | Schneider | MICOM P841 |  | Numerik | 2021
PHT.110 | 110 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#1 | #1 | Eksternal | GIS 150KV LONTAR | PHT 150kV DADAP #1 | NR | CZX-22 |  | Numerik |  |  |  | 1 |  | 40
PHT.111 | 111 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#2 | #2 | Eksternal | GIS 150KV LONTAR | PHT 150kV DADAP #2 | NR | CZX-22 |  | Numerik |  |  |  | 1 |  | 40
PHT.112 | 112 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#1 | #1 | Eksternal | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #1 | NR | CZX-22 |  | Numerik |  |  |  | 1 |  | 40
PHT.113 | 113 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#2 | #2 | Eksternal | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU #2 | NR | CZX-22 |  | Numerik |  |  |  | 1 |  | 40
PHT.114 | 114 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#1 | #1 | Internal | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #1
PHT.115 | 115 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#2 | #2 | Internal | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI #2
PHT.116 | 116 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#1 | #1 | Tidak Aktif | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #1
PHT.117 | 117 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#2 | #2 | Tidak Aktif | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU #2
PHT.118 | 118 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#1 | #1 | Internal | GI 150KV CENGKARENG | PHT 150kV TANGERANG #1 | Siemens | 7SL87 |  | Numerik | 2021 |  |  | 3 s |  | 40 s
PHT.119 | 119 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#2 | #2 | Internal | GI 150KV CENGKARENG | PHT 150kV TANGERANG #2 | Siemens | 7SL87 |  | Numerik | 2021 |  |  | 3 s |  | 40 s
PHT.120 | 120 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#1 | #1 | Tidak Aktif | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #1
PHT.121 | 121 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#2 | #2 | Tidak Aktif | GI 150KV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA #2
PHT.122 | 122 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#1 | #1 | Tidak Aktif | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #1
PHT.123 | 123 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#2 | #2 | Tidak Aktif | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG #2
PHT.124 | 124 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV ITS | #1 | Internal | GI 150KV CENGKARENG BARU | PHT 150kV ITS
PHT.125 | 125 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 | Internal | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU
PHT.126 | 126 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#1 | #1 | Tidak Aktif | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #1
PHT.127 | 127 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#2 | #2 | Tidak Aktif | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA #2
PHT.128 | 128 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#1 | #1 | Tidak Aktif | GI 150KV CILEDUG | PHT 150kV METLAND #1
PHT.129 | 129 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#2 | #2 | Tidak Aktif | GI 150KV CILEDUG | PHT 150kV METLAND #2
PHT.130 | 130 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#1 | #1 |  | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #1 | Alsthom | MVTR | 588657C, 588658C | Elektromekanik
PHT.131 | 131 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#2 | #2 |  | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG #2 | Alsthom | MVTR | 588656C, 588655C | Elektromekanik
PHT.132 | 132 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV LMK | #1 |  | GI 150KV DURIKOSAMBI | PHT 150kV LMK | Alsthom | LFAA 101 | 62047BF | Elektromekanik
PHT.133 | 133 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#1 | #1 | Eksternal | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #1 | Alsthom | LFAA 101 |  | Elektromekanik
PHT.134 | 134 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#2 | #2 | Eksternal | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU #2 | Alsthom | LFAA 101 |  | Elektromekanik
PHT.135 | 135 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#1 | #1 | Tidak Aktif | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #1
PHT.136 | 136 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#2 | #2 | Tidak Aktif | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK #2
PHT.137 | 137 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#1 | #1 | Tidak Aktif | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #1
PHT.138 | 138 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#2 | #2 | Tidak Aktif | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN #2
PHT.139 | 139 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#1 | #1 |  | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #1 | Alsthom | LFAA 101 | 315994J | Elektromekanik |  |  |  | 0.8 |  | 40
PHT.140 | 140 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#2 | #2 |  | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT #2 | Alsthom | LFAA 101 | 315995J | Elektromekanik |  |  |  | 0.8 |  | 40
PHT.141 | 141 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#1 | #1 | Internal | GI 150KV TANGERANG | PHT 150kV CENGKARENG #1 | Siemens | 7SL87 |  | Numerik | 2021 |  |  | 3 s |  | 40 s
PHT.142 | 142 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#2 | #2 | Internal | GI 150KV TANGERANG | PHT 150kV CENGKARENG #2 | Siemens | 7SL87 |  | Numerik | 2021 |  |  | 3 s |  | 40 s
PHT.143 | 143 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#1 | #1 | Internal | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #1 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 s |  | 40 s
PHT.144 | 144 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#2 | #2 | Internal | GI 150KV TANGERANG | PHT 150kV JATAKE BARU #2 | NR | PCS-931 |  | Numerik | 2021 |  |  | 1 s |  | 40 s
PHT.145 | 145 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#1 | #1 | Tidak Aktif | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #1
PHT.146 | 146 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#2 | #2 | Tidak Aktif | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG #2
PHT.147 | 147 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | Tidak Aktif | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #1
PHT.148 | 148 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | Tidak Aktif | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG #2
PHT.149 | 149 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#1 | #1 | Tidak Aktif | GIS 150KV KEMBANGAN | PHT 150kV METLAND #1
PHT.150 | 150 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#2 | #2 | Tidak Aktif | GIS 150KV KEMBANGAN | PHT 150kV METLAND #2
PHT.151 | 151 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#1 | #1 | Tidak Aktif | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #1
PHT.152 | 152 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#2 | #2 | Tidak Aktif | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI #2
PHT.153 | 153 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#1 | #1 | Tidak Aktif | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #1
PHT.154 | 154 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#2 | #2 | Tidak Aktif | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN #2
PHT.155 | 155 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#1 | #1 | Internal | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #1
PHT.156 | 156 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#2 | #2 | Internal | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN #2
PHT.157 | 157 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#1 | #1 | Tidak Aktif | GIS 150KV METLAND | PHT 150kV KEMBANGAN #1
PHT.158 | 158 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#2 | #2 | Tidak Aktif | GIS 150KV METLAND | PHT 150kV KEMBANGAN #2
PHT.159 | 159 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#1 | #1 | Tidak Aktif | GIS 150KV METLAND | PHT 150kV CILEDUG #1
PHT.160 | 160 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#2 | #2 | Tidak Aktif | GIS 150KV METLAND | PHT 150kV CILEDUG #2
PHT.161 | 161 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#1 | #1 | Tidak Aktif | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #1
PHT.162 | 162 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#2 | #2 | Tidak Aktif | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA #2
PHT.163 | 163 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#1 | #1 | Tidak Aktif | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #1
PHT.164 | 164 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#2 | #2 | Tidak Aktif | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG #2
PHT.165 | 165 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1
PHT.166 | 166 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2
PHT.167 | 167 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1
PHT.168 | 168 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2
PHT.169 | 169 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL #1
PHT.170 | 170 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN #2
PHT.171 | 171 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #1
PHT.172 | 172 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | Eksternal | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG #2
PHT.173 | 173 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1
PHT.174 | 174 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2
PHT.175 | 175 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1
PHT.176 | 176 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2
PHT.177 | 177 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1
PHT.178 | 178 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2
PHT.179 | 179 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #1
PHT.180 | 180 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI #2
PHT.181 | 181 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #1
PHT.182 | 182 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA #2
PHT.183 | 183 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #1
PHT.184 | 184 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | Eksternal | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL #2

## HEL_PHT_SET (hidden)
ID | SEGMEN A | SEGMEN B | SRC | TIPE | LISTING
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140
|  |  | https://docs.google.com/spreadsheets/d/1ZKPej-AGG0QtAnPVT1f1-UdGKVZ6JPwo-SlTcIef0Cw/edit?usp=drive_link | MICOM P545 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P546 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P543 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P521 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1qTIqpv3M4b7ZRFh1Fll3GEGWXwiKFHTKElCF1MX9Cx0/edit?gid=544152550#gid=544152550 | MICOM P443 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail and I< | Supervision | System Check | Autoreclose |  | Parameter | Phase CT Primary | Main VT Primary | Distance Element | Line Length | Line Impedance | Line Angle | kZ Res Comp | kZ Res Angle | Z1 | R1G | R1Ph | tZ1 | Z2 | R2G | R2Ph | tZ2 | Z3 | R3G | R3Ph | tZ3 |  |  |  |  | Distance Scheme | Program Mode | Standard Mode | Aid Dist. Dly | tReversal Guard | Unblocking Logic | SOTF/TOR Mode | SOTF Delay | Z1Ext Fail | Power Swing | Delta R | Delta X | IN> Status | Superviion | VTS Mode | CTS Mode | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Chk scheme A/R | C/S Sheck Scheme for Man CB | V<Dead Line | V<Live Line | V<Dead Bus | V<Live Bus | Diff Voltage | Diff Frequency | Diff Phase |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [16 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 20-01-2022 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P442 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail and I< | Supervision | System Check | Autoreclose |  | Parameter | Phase CT Primary | Main VT Primary | Distance Element | Line Length | Line Impedance | Line Angle | kZ Res Comp | kZ Res Angle | Z1 | R1G | R1Ph | tZ1 | Z2 | R2G | R2Ph | tZ2 | Z3 | R3G | R3Ph | tZ3 |  |  |  |  | Distance Scheme | Program Mode | Standard Mode | Aid Dist. Dly | tReversal Guard | Unblocking Logic | SOTF/TOR Mode | SOTF Delay | Z1Ext Fail | Power Swing | Delta R | Delta X | IN> Status | Superviion | VTS Mode | CTS Mode | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Chk scheme A/R | C/S Sheck Scheme for Man CB | V<Dead Line | V<Live Line | V<Dead Bus | V<Live Bus | Diff Voltage | Diff Frequency | Diff Phase |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [16 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 20-01-2022 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P446 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail and I< | Supervision | System Check | Autoreclose |  | Parameter | Phase CT Primary | Main VT Primary | Distance Element | Line Length | Line Impedance | Line Angle | kZ Res Comp | kZ Res Angle | Z1 | R1G | R1Ph | tZ1 | Z2 | R2G | R2Ph | tZ2 | Z3 | R3G | R3Ph | tZ3 |  |  |  |  | Distance Scheme | Program Mode | Standard Mode | Aid Dist. Dly | tReversal Guard | Unblocking Logic | SOTF/TOR Mode | SOTF Delay | Z1Ext Fail | Power Swing | Delta R | Delta X | IN> Status | Superviion | VTS Mode | CTS Mode | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Chk scheme A/R | C/S Sheck Scheme for Man CB | V<Dead Line | V<Live Line | V<Dead Bus | V<Live Bus | Diff Voltage | Diff Frequency | Diff Phase |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [16 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 20-01-2022 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/15M9aJzZzNu5hlgrMke4A-x8s0Bqc0Sw3YQzyredDJcI/edit?usp=drive_link | L90 | Parameter | AC Inputs | Current | Voltage | Grouped Element/Group 1 | Current Differential | Function | Pickup | Restrain 1 | Restrain 2 | Breakpoint | 87L Current Diff Gnd Function | Stub Bus | Line Pickup | Function | Phase IOC Line Pickup | UV Pickup | Phase Distance | Phase Distance Z1 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Phase Distance Z2 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | [5 empty] | Parameter | Phase Distance Z3 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Ground Distance Z1 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Ground Distance Z2 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Ground Distance Z3 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | [5 empty] | Parameter | Power Swing Detect | Load Encroachment | Phase Current | Phase TOC | Phase IOC | Phase Directional | Neutral Current | Neutral IOC | Phase IOC | Neutral Directional IOC | Transient Ground Fault | Wattmetric Ground Fault | Ground Current | Ground TOC | Ground IOC | Negative Sequence Current | Negative Sequence TOC | Negative Sequence IOC | Negative Sequence Directional | Breaker Failure | Voltage Element | Supervising Element | Disturbance Detector | 87L Trip | Underfrequency | Overfrequency | Thermal Overload Prot | Pilot Scheme |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | Jenis Relay | Tipe Relay | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1x8x8zV4t51Gk41JCc78MVuYC3wnSzjAg3csMLBbGVL8/edit?usp=drive_link | 7SL87 | Parameter | CT | VT | General | C1 Per Length | C0 Per Length | X Per Length | Kr / Kx | Line Length | Line Angle | 87 Line Differential | I-DIFF | Threshold | Operate Delay | I-DIFF Fast | Threshold | IC-Compensation | Mes. V failure | Mode | Asym. Fail. -time delay | 68 P.swing | Zones to be blocked | 50/51 O/C Gnd -A | Mode | 21 Distance Prot. | Dist. Characteristic Angle | Z1 | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z2 | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z3 | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z1 (Mho) | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z2 (Mho) | X Reach | [5 empty] | Parameter | R (Ph-g) | R (Ph-ph) | Z3 (Mho) | X Reach | R (Ph-g) | R (Ph-ph) | 50 OC highspeed | Switch onto Fault | Configuration | Mode | Operate Delay | Aided Scheme | Send With | Operate With | Mode | Send prolongation |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 14-12-2018 | [23 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 12-07-2018 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [9 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1HmSu_VUPIme2KvbscEGPdfpsM5rONe6A_eINQFARbH4/edit?usp=drive_link | 7SD61 | Parameter | CT | VT | General | C1 Per Length | C0 Per Length | X Per Length | Kr / Kx | Line Length | Line Angle | 87 Line Differential | I-DIFF | Threshold | Operate Delay | I-DIFF Fast | Threshold | IC-Compensation | Mes. V failure | Mode | Asym. Fail. -time delay |  |  | 50/51 O/C Gnd -A | Mode |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [18 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1X6YT1INoslajhA2bTFUi7EPXzoylquoFS_azi6Oih8Q/edit?usp=drive_link | RED670 | Parameter | CT | VT | Diff Mode | IdMin | EndSection1 | EndSection2 | SlopeSection2 | SlopeSection3 | IdMinHigh | tIdMinHigh | I2/I1Ratio | I5/I1Ratio | OpenCTEnable | tOCTResetDelay | LossSynEn | Setting Group 1 | RLdFw | RLdFwMax | RLdFwMin | RStart | XStart | ArgLd | ArgDir | ArgNegRes | Zone 1 | tPP | X1PPZ1 | R1PPZ1 | X1PEZ1 | X1PEZ1 | X0Z1 | R0Z1 | RFPPZ1 | RFPEZ1 | tPPZ1 | Zone 2 | X1Z2 | R1Z2 | X0Z2 | R0Z2 | [5 empty] | Parameter | RFPPZ2 | RFPEZ2 | tPPZ2 | Zone 3 | X1Z3 | R1Z3 | X0Z3 | R0Z3 | RFPPZ3 | RFPEZ3 | tPPZ3 | Automatic SOTF | Operation | AutoInitMode | Power Swing Detection | Operation | Fault Locator | R1A | X1A | R1B | X1B | R1L | X1L | R0L | X0L | LineLength | Scheme Communication | SchemeType | tSecurity | Current Protection | EF4PTOC : 1 | Operation | DirMode1 | Fuse Failure | Operation | OpMode | Autorecloser | Operation | CBReady Tpe | t1 1Ph | t1 3Ph | Synchronizing | OperationSynch |  |  |  |  | Parameter | UDiff Synch | FreqDiffMax | CloseAngleMax |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) |  | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1bG5rOiNz_-liuI3ZWq6e9w0Pvo9SQmXx2tLZR0kWhyU/edit?usp=drive_link | PCS-931 | Parameter | U1n/U2n | I1n_Base/I2n_Base | Line Setting | X1L | R1L | X0L | R0L | X0M | R0M | Line Length | Diff Setting | 87L.I_Pkp | 87L.K_Cr_CT | 87L.En | 87L.En_Neutral | Dist Setting | 21-1.Real_k0 | 21-1.Imag_k0 | 21-1.phi1_Reach | 21M1.ZG.Z_Set | 21M1.ZG.t_Op | 21M1.ZP.Z_Set | 21M1.ZP.t_Op | 21M2.ZG.Z_Set | 21M2.ZG.t_Op | 21M2.ZP.Z_Set | 21M2.ZP.t_Op | 21M3.ZG.Z_Set | 21M3.ZG.t_Op | 21M3.ZP.Z_Set | 21M3.ZP.t_Op | 21M.Pilot.Z_Set | 21M.PSBR (silangi yang tidak bernilai 1) | 85.Opt_PilotMode | Additional | 50/51Gx.En | 21SOTF.En | 78.En_Trp (OOS) | 50/51G1.En/sejenisnya | 50/51P1.En/sejenisnya | 85.DEF.En | VTS.En | CB1.25.En_SynChk | CB1.25.En_NoChk | CB1.79.En | AR Mode |  |  |  |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  |  | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) |  | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/19botCaaavxDBaf-vARrZlUhyojcuz9Rbbh_3pnyAtjE/edit?usp=drive_link | GRL 200 | Parameter | Analog Input | CT | VT | Fault Locator | FL_EN | FL_1Line_km | FL_1X1 | FL_1R1 | FL_1X0 | FL_1R0 |  | Distance | ZS-Chara | PSBSZ | LES-EN | LESR | LESR-Angle | Z1S-Mho.Angle | Z1S-Mho.Reach | TZ1S | Z2S-Mho.Angle | Z2S-Mho.Reach | TZ2S | Z3S-Mho.Angle | Z3S-Mho.Reach | TZ3S | ZG-Chara | PSBGZ | LEG-EN | LEGR | LEGR-Angle | Z1G-X.Reach | Z1G-R.Angle | Z1G-R.Reach | TZ1G | Z2G-X.Reach | Z2G-R.Angle | Z2G-R.Reach | TZ2G | Z3G-X.Reach | [5 empty] | Z3G-R.Angle | Z3G-R.Reach | TZ3G | Carrier Distance | Dis-CAR | TREBK-Dis | Carrier DEF | DEF-CAR | TDEFCF | TREBK-DEF | EF | EF1-EN | EF2-EN | SOTFOC-EN | VTF1-EN | CTF-EN | ARC1-EN | ARC1-MODE | MPAR-MODE | ARC1-VCHK-EN | SYN1-dV | SYN1-dfEN | SYN1-df | Differential | DIFL_EN | DIFL-I1 | DIFL-I2 | DIFL-Slope 1 | DIFL-Slope 2 | DIFL-IcC.En | TDIFL | DIFL-RDIF-EN | DIFL-IdSV-EN | DIFL-CTFBlk | DIFLFS-EN | DIFL-ARCBlk | DIFL-TPMD |  |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [11 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
PHT.01 | ANGKE | ANCOL | https://docs.google.com/spreadsheets/d/1_feMC27xQFEnCmytl4JDOBOWFZPWBcca_pqeWjEp_Wc/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 2000 / 5 A | 150 kV / 100 V | 4.6 km | 0.33 ohm | 70 deg | 0.654 | 3.382 deg |  | 1 A | 10 A | 30% | 150% | 0 s |  |  | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | 100 ms | Disabled |  | Enable Pole Dead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | I Diff |  |  | 0.264 ohm | 70 deg | 5.46 ohm | 0.404 ohm | 70 deg | 6.06 ohm | 0.952 ohm | 70 deg | 6.74 ohm |  | 1PAR/3PAR | BAR 3 Phase | 100 ms | 1 s | 3 s |  | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000-05-01 |  | 5,15 | 0,42 | - | - |  | 0,85 | 0.685 | - | - | - | -
PHT.02 | ANGKE | ANCOL | https://docs.google.com/spreadsheets/d/1ZKPej-AGG0QtAnPVT1f1-UdGKVZ6JPwo-SlTcIef0Cw/edit?usp=drive_link | MICOM P545 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000-05-01 |  | 5,15 | 0,42 | - | - |  | 0,85 | 0.685 | - | - | - | -
PHT.03 | ANGKE | KARET LAMA | https://docs.google.com/spreadsheets/d/1qTIqpv3M4b7ZRFh1Fll3GEGWXwiKFHTKElCF1MX9Cx0/edit?gid=544152550#gid=544152550 | MICOM P443 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 4000 / 5 A | 150 kV / 100 V |  | 7.9 km | 1.296 ohm | 78 deg | 0.59 | -5 deg | 1.036 ohm | 10.77 ohm | 10.77 ohm | 0 s | 1.554 ohm | 11.97 ohm | 11.97 ohm | 0.8 s | 2.826 ohm | 13.30 ohm | 13.30 ohm | 1.6 s | [6 empty] | PUR | 0 s | - | - | Enabled Pole Dead / Enabled | 30 s | Disabled | Blocking | - | - | - |  | Measured + MCB | Disabled |  | 1PAR/3PAR | BAR 3 Phase | 0.1 s | 1 s | 3 s |  |  |  | 11.5 V | 52 V | 11.5 V | 52 V | 6 V | 0.165 Hz | 15 deg | [20 empty] | OCR/GFR | GE ALSTOM - MICOM P142 |  | Setting Terpasang | 4000 / 5 A |  | 3.75 A | 0.375 SI | Disabled | - |  | 0.65 A | 0.66 SI | Disabled | - | Disabled | Disabled
PHT.04 | ANGKE | KARET LAMA | https://docs.google.com/spreadsheets/d/1qj6Lzay1QbYrp03gjdLecJRnw8A2fSOiQGGwjEc1-RE/edit?usp=drive_link | MICOM P443 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 4000 / 5 A | 150 kV / 100 V |  | 7.9 km | 1.296 ohm | 78 deg | 59% | -5 deg | 1.036 ohm | 10.77 ohm | 10.77 ohm | 0 s | 1.554 ohm | 11.97 ohm | 11.97 ohm | 0.8 s | 2.826 ohm | 13.30 ohm | 13.30 ohm | 1.6 s | [6 empty] | PUR | 0 s | - | - | Enabled Pole Dead / Enabled | 30 s | Disabled | Blocking | - | - | - |  | Measured + MCB | Disabled |  | 1PAR/3PAR | BAR 3 Phase | 0.1 s | 1 s | 3 s |  |  |  | 11.5 V | 52 V | 11.5 V | 52 V | 6 V | 0.165 Hz | 15 deg | [20 empty] | OCR/GFR | GE ALSTOM - MICOM P142 |  | Setting Terpasang | 4000 / 5 A |  | 3.75 A | 0.375 SI | Disabled | - |  | 0.65 A | 0.66 SI | Disabled | - | Disabled | Disabled
PHT.05 | ANGKE | KETAPANG | https://docs.google.com/spreadsheets/d/1MGuDnJQjAXaXIgYMsUYepUsSRu-UBFbbFhzmkb2QyWs/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000 / 5 A | 150 kV / 100 V | 5.5 km | 0,244 ohm | 82 deg | 0.64 | -35 deg |  | 1 A | 10 A | 30% | 150% | 0 s | DIsabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | POR | 100 ms | Disabled | - | Enabled PoleDead | 000011 | Disabled | 200 ms | - |  | Measured + MCB | Standard | Disabled |  | 0.194 ohm | 82 deg | 7.949 ohm | 0.292 ohm | 82 deg | 9.93 ohm | 0.442 ohm | 82 ohm | 12.42 ohm |  | Not Active | - | - | - | - |  | 47.5 V | 10.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000 / 5 A |  | 1.5 A | 0.58 SI | Disabled | - |  | 0.25 A | 0.905 SI | Disabled | - | Disabled | Disabled
PHT.06 | ANGKE | KETAPANG | https://docs.google.com/spreadsheets/d/185vGIM_krvzVjYEP75fefF7QNys4Z1ciW9-THtsqxIU/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000 / 5 A | 150 kV / 100 V | 5.5 km | 0.232 ohm | 57 deg | 0.64 | -4 deg |  | 1 A | 10 A | 30% | 150% | 0 s | DIsabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | POR | 100 ms | Disabled | - | Enabled PoleDead | 000011 | Disabled | 200 ms | - |  | Measured + MCB | Standard | Disabled |  | 0.186 ohm | 57 deg | 13.44 ohm | 0.334 ohm | 57 deg | 16.8 ohm | 0.556 ohm | 57 deg | 20.41 ohm |  | Not Active | - | - | - | - |  | 47.5 V | 10.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000 / 5 A |  | 0.7 A | 0.735 SI | 7 A | 0.15 DT |  | 0.25 A | 0.905 SI | 1 A | 1 SI | Disabled | Disabled
PHT.07 | ANGKE | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1HmSu_VUPIme2KvbscEGPdfpsM5rONe6A_eINQFARbH4/edit?usp=drive_link | 7SD61 | Setting Terpasang | 2000-05-01 | 150 kv/100 v |  | NA | NA | NA | NA | NA | NA |  | ON | 1A | 0 | ON | 10 | N/A |  | NA |  |  |  |  | OFF | [22 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000 / 5 A |  | 3.6 A | 0.48 SI | Block | - |  | 0.6 A | 0.75 SI | Block | -
PHT.08 | ANGKE | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/117KSkWV1SUcCvwWvQBe-7qtydrWoDf3LTLqZ-cRBxKc/edit?usp=drive_link | 7SD61 | Setting Terpasang | 2000-05-01 | 150 kv/100 v |  | NA | NA | NA | NA | NA | NA |  | ON | 1A | 0 | ON | 10 | N/A |  | NA |  |  |  |  | OFF | [22 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000 / 5 A |  | 3.6 A | 0.48 SI | Block | - |  | 0.6 A | 0.75 SI | Block | -
PHT.09 | ANGKE | UGC MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1x8x8zV4t51Gk41JCc78MVuYC3wnSzjAg3csMLBbGVL8/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | SIEMENS - 7SJ82 |  | Setting Terpasang | 2000-05-01 |  | 5.25 A | 0.43 SI | Disabled | - |  | 0.88 A | 0.52 SI | Disabled | - | - | -
PHT.10 | ANGKE | UGC MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1DaMcxhO1EMx3VFiwcgC0WLlbavsPToE4IZhuJotgdj0/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | SIEMENS - 7SJ82 |  | Setting Terpasang
PHT.11 | DADAP | LONTAR | https://docs.google.com/spreadsheets/d/1zb-AMDz1Y4yx4LJ4kQxYhfEuYM5_UQ_h1MXrHngQqOk/edit?usp=drive_link | MICOM P446 | Setting Terpasang |  | Enabled | Enabled | Disabled | N/A | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 767011 | 150kV/100 V |  | 26,26 km | 19,92 ohm | 83 deg | 0,68 | -8 | 15,93 ohm | 34,26 ohm |  | 0 | 23,90 ohm | 38,07 |  | 0,4 | 43,21 ohm | 42,30 ohm |  | 1.6 s | [7 empty] | 0 |  |  | Enable Polde Dead | 30 s |  | Blocking |  |  |  |  | Measure + MCB | Disable |  | 1PAR/3PAR | Bar 3 Phase | 0,1 | 1 s | 3 s |  |  | Enable | 11,5 | 52 | 11,5 | 52 | 6 v | 0,167 | 15 | [20 empty] | OCR/GFR | GE Alstom - Micom P841 |  | Setting Terpasang | 4000/1 A |  | 0,82 | 0,295 | Disable | Disable |  | 0,14 | 0,6 | Disable | Disbale | Disable | Disbale | [17 empty] | TJBB/01/04/2020/27
PHT.12 | DADAP | LONTAR | https://docs.google.com/spreadsheets/d/1WVN2za7lQTd2VIPIs-tTixzcZxSU8MZTMqM7oTBrCr8/edit?usp=drive_link | MICOM P446 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 767011 | 150kV/100 V |  | 26,26 km | 19,92 ohm | 83 deg | 0,68 | -8 | 15,93 ohm | 34,26 ohm |  | 0 | 23,90 ohm | 38,08 |  | 0,4 | 43,20 ohm | 42,29 ohm |  | 1.6 s | [7 empty] | 0 |  |  | Enable Polde Dead | 30 s |  | Blocking |  |  |  |  | Measure + MCB | Disable |  | 1PAR/3PAR | Bar 3 Phase | 0,1 | 1 s | 3 s |  |  | Enable | 11,5 | 52 | 11,5 | 52 | 6 V | 165 | 15 | [20 empty] | OCR/GFR | GE Alstom - Micom P841 |  | Setting Terpasang | 4000/1 A |  | 0,82 | 0,295 | Disable | Disbale |  | 0,14 | 0,6 | Disable | Disbale | Disable | Disbale | [17 empty] | TJBB/01/04/2020/27
PHT.13 | DADAP | TELUK NAGA | https://docs.google.com/spreadsheets/d/1_7zzuc3kqP8gs0-RvMQZqs__EvVgSALJYksmlBl7RXU/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 767011 | 150 KV/ 100 V | 6,13 | 4,65 ohm | 83 deg | 0,68 | -7 |  | 0,2 | 2 | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 | 0,4 | 1,6 | PUR | 0 | Disable | - | Enable Pole Dead | 000011 | Enable | 000011 |  |  | Measure + MCB | Disable | - |  | 3,72 ohm | 83 deg |  | 8,15 ohm | 83 deg |  | 13,89 | 83 |  |  | 1PAR/3PAR | BAR 3 PHASE | 0,1 | 1 S | 3 S |  | 52 | 11,5 | enable | V< | enable | 15 | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | GE Alstom - Micom P841 |  | Setting Terpasang | 4000/1A | Group 1 | 0.82 | 0.295 | - | - | Group 1 | 0.14 | 0.6 | - | - | - | - | [17 empty] | TJBB/01/04/2020/27
PHT.14 | DADAP | TELUK NAGA | https://docs.google.com/spreadsheets/d/1UBstAMlW87TlYf7d0kKptpIhB2xdTGBqKn6_ih40fMc/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 767011 | 150 KV/ 100 V | 6,13 | 4,65 ohm | 83 deg | 0,68 | -7 |  | 0,2 | 2 | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 | 0,4 | 1,6 | PUR | 0 | Disable | - | Enable Pole Dead | 000011 | Enable | 000011 |  |  | Measure + MCB | Disable | - |  | 3,72 ohm | 83 deg |  | 8,15 ohm | 83 deg |  | 13,89 | 83 |  |  | 1PAR/3PAR | BAR 3 PHASE | 0,1 | 1 S | 3 S |  | 52 | 11,5 | enable | V< | enable | 15 | 6 V | 165 | [11 empty] | OCR/GFR | GE Alstom - Micom P841 |  | Setting Terpasang | 4000/1A | Group 1 | 0.82 | 0.295 | - | - | Group 1 | 0.14 | 0.6 | - | - | - | - | [17 empty] | TJBB/01/04/2020/27
PHT.15 | MUARAKARANG BARU | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1VxGLKtNFrq3w9160PxX92v0ZfUJC78lcZZT4I8wEaSo/edit?usp=sharing | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2500 / 5 A | 150 kV / 100 V | 0.26 km | 0.014 ohm | 73 deg | 0.72 | -11 deg |  | 1.5 A | 10 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | Measured + MCB | Standard | Disabled |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6.5 V | 0.17 Hz | [11 empty] | OCR/GFR | NR - PCS9611S |  | Setting Terpasang | 219268 | 50/51P4 | 4.8 A | 0.469 SI | - | - | 50/51G4 | 0.8 A | 0.808 SI | - | - | Disabled | Disabled
PHT.16 | MUARAKARANG BARU | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/14NcijQiUUUrJNgxaXrzHMIV1i8qESxkADZbLcfES6KY/edit?usp=sharing | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2500 / 5 A | 150 kV / 100 V | 0.26 km | 0.014 ohm | 73 deg | 72% | -11 deg |  | 1.5 A | 10 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | Measured + MCB | Standard | Disabled |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6.5 V | 0.17 Hz | [11 empty] | OCR/GFR | NR - PCS9611S |  | Setting Terpasang | 219268 | 50/51P4 | 4.8 A | 0.469 SI | - | - | 50/51G4 | 0.8 A | 0.808 SI | - | - | Disabled | Disabled
PHT.17 | MUARAKARANG BARU | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1CHCZRetMGgeFImQEF7NwZNsFlRUGwfJ-bQn8Or5-20o/edit?usp=drive_link | MICOM P521 | Setting Terpasang |  | Enabled | N/A | N/A | Enabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | N/A | N/A | N/A | Disabled | Disabled | Disabled | Disabled |  | Setting Terpasang | 4000 / 5 A | N/A | - | - | - | - |  |  | 0.2 In | 2 In | 30% | 150% | 0 s | No | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | AREVA - MICOM P521 |  | Setting Terpasang | 4000 / 5 A |  | 0.51 In | 0.650 (SI) | - | - |  | - | - | - | - | - | -
PHT.18 | MUARAKARANG BARU | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/17jLKzetQ5moSvleindl6n0VJnd_pB_bBMhqmPA0ccus/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 4000 / 5 A | 150 kV / 100 V | 0.7 km | 0.2 ohm | 82 deg | 0.68 | -7 deg |  | 1.5 A | 5 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | Measured + MCB | IDiff+Std | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | ALSTOM - MICOM P543 |  | Setting Terpasang | 4000 / 5 A | Enabled | 2.55 A | 0.65 (SI) | - | - | Disabled | - | - | - | - | Disabled | Disabled
PHT.19 | MUARAKARANG LAMA | ANGKE | https://docs.google.com/spreadsheets/d/1bU3CdLZuuvrfJQ9RiGxwRfx0ck10eRFG9B1VYpZvYCU/edit?usp=drive_link | 7SD61 | Setting Terpasang | 2000-05-01 | 150 kv/100 v |  | NA | NA | NA | NA | NA | NA |  | ON | 1A | 0 | ON | 10 | N/A |  | NA |  |  |  |  | OFF | [22 empty] | OCR/GFR | SIEMENS - 7SJ62 |  | Setting Terpasang | 2000 / 5 A |  | 5,25 A | 0,45 SI | Disabled | - |  | 0,875 A | 0,79 SI | Disabled | - | Disabled | Disabled
PHT.20 | MUARAKARANG LAMA | ANGKE | https://docs.google.com/spreadsheets/d/1YPIrB_myuVj18UC9n3sQMVCPOFOWGoNdFJUiSzP21ZU/edit?usp=drive_link | 7SD61 | Setting Terpasang | 2000-05-01 | 150 kv/100 v |  | NA | NA | NA | NA | NA | NA |  | ON | 1A | 0 | ON | 10 | N/A |  | NA |  |  |  |  | OFF | [22 empty] | OCR/GFR | SIEMENS - 7SJ62 |  | Setting Terpasang | 2000 / 5 A |  | 5,25 A | 0,45 | Disabled | - |  | 0,875 A | 0,79 | Disabled | - | Disabled | Disabled
PHT.21 | MUARAKARANG LAMA | BUDIKEMULYAN | https://docs.google.com/spreadsheets/d/1yexP-aydoUDEUEuEoWyp19xlAZ0COr0NnYs18Osgp_U/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Group 1 | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 150kV/100V | 1200/5 A | 14 km | 0.26 ohm | 72.87 deg | 0.772 | -17.235 deg |  | 0.61 A | 6.13 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 0.21 ohm | 72.87 deg | 6.61 ohm | 0.31 ohm | 72.87 deg | 7.35 ohm | 0.43 ohm | 72.87 deg | 8.16 ohm |  | Not Active | - | - | - | - |  | - | - | Disabled | - | - | - | - | - | [11 empty] | OCR/GFR | SIEMENS - 7SJ62 |  | Setting Terpasang | 1200 / 5 A |  | 3.675 A | 0.628 SI | Block | - |  | 0.615 A | 0.975 SI | Block | -
PHT.22 | MUARAKARANG LAMA | BUDIKEMULYAN | https://docs.google.com/spreadsheets/d/1Pb8of-UR7UstAUi76PlEND2272bwV-msDOVxiUp8STY/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Group 1 | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 150kV/100V | 1200/5 A | 14 km | 0.26 ohm | 72.87 deg | 0.772 | -17.235 deg |  | 0.61 A | 6.13 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 0.21 ohm | 72.87 deg | 6.61 ohm | 0.31 ohm | 72.87 deg | 7.35 ohm | 0.43 ohm | 72.87 deg | 8.16 ohm |  | Not Active | - | - | - | - |  | - | - | Disabled | - | - | - | - | - | [11 empty] | OCR/GFR | SIEMENS - 7SJ62 |  | Setting Terpasang | 1200 / 5 A |  | 3.675 A | 0.628 SI | Block | - |  | 0.615 A | 0.975 SI | Block | -
PHT.23 | MUARAKARANG LAMA | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1S2rihWhXy3w5Ww6MHGm6lgCA6W9oU9y_iOhuo-TucH0/edit?usp=drive_link | MICOM P521 | Setting Terpasang |  | Enabled | N/A | N/A | Enabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | N/A | N/A | N/A | Disabled | Disabled | Disabled | Disabled |  | Setting Terpasang | 2000 / 5 A | N/A | - | - | - | - |  |  | 0.5 In | 1 In | 60% | 150% | 0 s | No | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | NR / PCS 9611S |  | Setting Terpasang | 2000/5 A |  | 1 In | 0.541 SI | - | - |  | 0.167 In | 0.804 SI | - | -
PHT.24 | MUARAKARANG LAMA | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1fJKaIBpjVeSkgeh6v32tj35e4KKG3b6u9m04JV_aELA/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  | Setting Terpasang | 2000 / 5 A | 150 kV / 100 V | 0.7 km | 0.2 ohm | 82 deg | 0.68 | -7 deg |  | 3 A | 5 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | ALSTOM - MICOM P543 |  | Setting Terpasang | 2000/5 A |  | 1 In | 0.541 SI | - | - |  | 0.167 In | 0.804 SI | - | -
PHT.25 | MUARAKARANG LAMA | UGC ANGKE | https://docs.google.com/spreadsheets/d/1rbyqufWMloGUbWyrpwEyPX_u-cHww-6bFaYKw-T3Rt0/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000-05-01 | 150 kv/100 v |  | 1.763 uF/km | 1.763 uF/km | 0.0333 ohm/km | 1.39/0.67 | 3.6 km | 81.36 |  | ON | 1 | 0 | ON | 10 A | ON |  | ON | NO | OFF |  |  | OF | ON |  |  | 2.5 | 2.5 | 1.5 | 0 |  | 5 | 5 | 2.5 | 0.3 |  | 10 | 10 | 5 | 0.6 |  | 0.5 | NA | NA | 0.3 |  | 0.5 | [5 empty] | Setting Terpasang | NA | NA |  | 0.5 | NA | NA | NA |  | 21DISTANCE PROT.1.Z1,Z2,DISTANCE PROT MHO Z1,Z2 | OFF | 0 |  | NA | NA | NA | NA | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000 / 5 A |  | 5,25 A | 0,45 | Disabled | - |  | 0,875 A | 0,79 | Disabled | - | Disabled | Disabled
PHT.26 | MUARAKARANG LAMA | UGC ANGKE | https://docs.google.com/spreadsheets/d/1GhA89opUsE6DY2sgNZ1_11q9NqUSkgCehakKWigHir4/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000-05-01 | 150 kv/100 v |  | 1.763 uF/km | 1.763 uF/km | 0.0333 ohm/km | 1.39/0.67 | 3.6 km | 81.36 |  | ON | 1 | 0 | ON | 10 A | ON |  | ON | NO | OFF |  |  | OF | ON |  |  | 2.5 | 2.5 | 1.5 | 0 |  | 5 | 5 | 2.5 | 0.3 |  | 10 | 10 | 5 | 0.6 |  | 0.5 | NA | NA | 0.3 |  | 0.5 | [5 empty] | Setting Terpasang | NA | NA |  | 0.5 | NA | NA | NA |  | 21DISTANCE PROT.1.Z1,Z2,DISTANCE PROT MHO Z1,Z2 | OFF | 0 |  | NA | NA | NA | NA | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000 / 5 A |  | 5,25 A | 0,45 | Disabled | - |  | 0,875 A | 0,79 | Disabled | - | Disabled | Disabled
PHT.27 | DAAN MOGOT | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1X6YT1INoslajhA2bTFUi7EPXzoylquoFS_azi6Oih8Q/edit?usp=drive_link | RED670 | Setting Terpasang | [45 empty] | Setting Terpasang | [47 empty] | Setting Terpasang | [9 empty] | OCR/GFR | ABB - REF615 |  | Setting Terpasang | 3000/1 A |  | 1,01 | 0,34 | - | - |  | 0.168 | 0.619 | - | - | - | - | [10 empty] | TJBB/01/04/2019/151
PHT.28 | DAAN MOGOT | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1G3gsiHGK3LZk-LYVkMn4Lp_b20qWblsNuM-mr210khk/edit?usp=drive_link | RED670 | Setting Terpasang | [45 empty] | Setting Terpasang | [47 empty] | Setting Terpasang | [9 empty] | OCR/GFR | ABB - REF615 |  | Setting Terpasang | 3000/1 A |  | 1,01 | 0,34 | - | - |  | 0.17 | 0.62 | - | - | - | - | [10 empty] | TJBB/01/04/2019/151
PHT.29 | DAAN MOGOT | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1nF3Yb-cxvss-mTzXAisCXpRT-x9d3h7daUeEVFqLyfs/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 3000 / 1 A | 150 kV / 100 V | 4,6 km | 11,48 ohm | 81 deg | 0,66 | 5 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | POR | 0 s | Disabled | 0,1 s | Enabled PoleDead | 000110 | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 9,19 ohm | 81 deg | 28,22 ohm | 16,70 ohm | 81 deg | 35,26 ohm | 27,86 ohm | 81 deg | 44,08 ohm |  | 1PAR/3PAR | BAR 3 Phase | 1,5 s | 1 s | 3 s |  | 52 V | 11,5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0,17 Hz | [11 empty] | OCR/GFR | ABB - REF615 |  | Setting Terpasang | 3000/1 A |  | 1,01 | 0,34 | - | - |  | 0.17 | 0.64 | - | - | - | - | [17 empty] | TJBB/01/04/2019/152
PHT.30 | DAAN MOGOT | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1b8Ar6yu7d-JedzfZhqR2BYpxHEu0SyHQUtRoaXE3dck/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 3000 / 1 A | 150 kV / 100 V | 4,6 km | 11,48 ohm | 81 deg | 0,66 | 5 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | POR | 0 s | Disabled | 0,1 s | Enabled PoleDead | 000110 | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 9,19 ohm | 81 deg | 28,22 ohm | 16,70 ohm | 81 deg | 35,26 ohm | 27,86 ohm | 81 deg | 44,08 ohm |  | 1PAR/3PAR | BAR 3 Phase | 1,5 s | 1 s | 3 s |  | 52 V | 11,5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0,17 Hz | [11 empty] | OCR/GFR | ABB - REF615 |  | Setting Terpasang | 3000/1 A |  | 1,01 | 0,34 | - | - |  | 0.17 | 0.64 | - | - | - | - | [17 empty] | TJBB/01/04/2019/152
PHT.31 | GROGOL | GROGOL BARU | https://docs.google.com/spreadsheets/d/1Uj1gPjF81B0mSfMFdXGmpnwtd063LYrSFByThhgI600/edit?usp=drive_link | 7SL87 | Setting Terpasang | -109571 | 150 kV/100 V |  | 0.016 | 0.016 | 0.299 | 1.29/0.67 | 2 km | 82 deg |  | On | 0.2 | 0 | On | 2 A | On |  | On | 10 S |  | Z1, Z2, Z3, MHO 1, MHO 2, MHO 3 |  |  |  | 82 Deg |  | 0.479 | 23 ohm | 23 ohm | 0 s |  | 1.718 ohm | 25 ohm | 25 ohm | 0.4 s |  | 3,043 ohm | 28 ohm | 28 ohm | 1.6 s | [12 empty] | Setting Terpasang | [8 empty] | 21 Distance Prot 1 Z2, 21 Distance Prot 1 Z3, 21 Distance Prot 1 MHO 2, 21 Distance Prot 1 MHO 3 | On | 0 S |  | 21 Distance Z2, 21 Distance Z mho 2 | 21 Distance Z2, 21 Distance Z mho 2 | ON | 0,05 | [27 empty] | OCR/GFR | SCHENEIDER MICOM P142 |  | Setting Terpasang | 1600/1 A |  | 1,2 A | 0,35 (SI) | Disable | - |  | 0,2 A | 0,6 (SI) | Disable | - | - | - | [20 empty] | UITJBB/01/04/2019/264
PHT.32 | GROGOL | GROGOL BARU | https://docs.google.com/spreadsheets/d/1zEZexc5bkP17UqfqRgeoSB6PBIt_OpVXjYJdxr3rCqc/edit?usp=drive_link | 7SL87 | Setting Terpasang | -109571 | 150 kV/100 V |  | 0.016 | 0.016 | 0.299 | 1.29/0.67 | 2 km | 82 deg |  | On | 0.2 | 0 | On | 2 A | On |  | On | 10 S |  | Z1, Z2, Z3, MHO 1, MHO 2, MHO 3 |  |  |  | 82 Deg |  | 47.9% | 23 ohm | 23 ohm | 0 s |  | 1.718 ohm | 25 ohm | 25 ohm | 0.4 s |  | 3,043 ohm | 28 ohm | 28 ohm | 1.6 s | [12 empty] | Setting Terpasang | [8 empty] | 21 Distance Prot 1 Z2, 21 Distance Prot 1 MHO 2 | On | 0 S |  | 21 Distance Z2, 21 Distance Z mho 2 | 21 Distance Z2, 21 Distance Z mho 2 | ON | 0,05 | [27 empty] | OCR/GFR | SCHENEIDER MICOM P142 |  | Setting Terpasang | 1600/1 A |  | 1,2 A | 0,35 (SI) | Disable | - |  | 0,2 A | 0,6 (SI) | Disable | - | - | - | [20 empty] | UITJBB/01/04/2019/264
PHT.33 | GROGOL | TOMANG | https://docs.google.com/spreadsheets/d/16KyrtoLa4_wA5ncdvK-LACsFt6b4ckA0XP5vGzG2xwg/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150 kV/100 V | 4.11 | 0.830 ohm | 85 deg | 0.26 | 26 deg |  | 0.3 A | 2 A | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 | 0.4 s | 1.2 s | - | - | - | - | Enable Pole Dead | (Z2 Z3) | Enable | (Z2 Z3) | - |  | Measured + MCB | STD | - |  | 0,66 ohm | 85 | 39 | 1,19 ohm | 85 deg | 43 | 2,38 | 85 | 48 |  |  | - | - | - | - |  | 52 | 11,5 | ENABLE | V DIFF>> | ENABLE | 10 DEG | 5 V | 100 MHZ | [11 empty] | OCR/GFR | EASERGY P142 |  | Setting Terpasang | 2000/1 A |  | 0.72 | 0.36 | Block |  |  | 0.12 | 0.66 | BLOCK |  | - | - | [17 empty] | UITJBB/01/04/2019/
PHT.34 | GROGOL | TOMANG | https://docs.google.com/spreadsheets/d/15gmDhpZ_XTW0_Zka9m91Wvf9hcZFQWeeC1JR6TXVxzE/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150 kV/100 V | 4.11 | 0.830 ohm | 85 deg | 0.26 | 26 deg |  | 0.2 A | 2 A | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 | 0.4 s | 1.2 s | - | - | - | - | Enable Pole Dead | (Z2 Z3) | Enable | (Z2 Z3) | - |  | Measured + MCB | DISABLE | - |  | 0,66 ohm | 85 | 8 | 1,19 ohm | 85 deg | 15 | 1,99 ohm | 85 | 15 |  |  | - | - | - | - |  | 52 | 11,5 | ENABLE | V DIFF>> | ENABLE | 10 DEG | 5 V | 100 MHZ | [11 empty] | OCR/GFR | EASERGY P142 |  | Setting Terpasang | 2000/1 A |  | 0.72 | 0.36 | Block |  |  | 0.12 | 0.66 | BLOCK |  | - | - | [17 empty] | UITJBB/01/04/2019/
PHT.35 | GROGOL BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1TSpR3FNKHwccw-h73vjdljseZHj5xabxDaJdJMCM3zY/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000/1A | 150kV/100V |  | 0,016 uF / km | 0,016 uF / km | 0,374 ohm/km | 1,29 / 0,67 | 6,468 km | 82 deg |  | On | 0,2 A | 0 | On | 2 A | On |  | On | 10 s |  | - |  | Off |  | 82 deg |  | 1,937 ohm | 28 ohm | 28 ohm | 0 |  | 2,905 ohm | 32 ohm | 32 ohm | 0,8 s |  | 28,375 ohm | 35 ohm | 35 ohm | 1,6 s |  |  |  |  | 0 | [7 empty] | Setting Terpasang | [8 empty] | Distance Z2, Z3, Mho Z2, Mho Z3 | On | 0 |  | Distance Z2, Mho Z2 | Distance Z2, Mho Z2 | On | 0,05 s | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000/1A |  | 0,97 A | 0,44 (SI) | Block | - |  | 0,16 A | 0,71 (SI) | Block | - | - | - | [20 empty] | UITJBB/01/04/2019/257
PHT.36 | GROGOL BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1gJ5AmkFJ6o12Zf8eFWzPGKFDOTg1B8bLkB721FSdClI/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000/1A | 150kV/100V |  | 0,016 uF / km | 0,016 uF / km | 0,374 ohm/km | 1,29 / 0,67 | 6,468 km | 82 deg |  | On | 0,2 A | 0 | On | 2 A | On |  | On | 10 s |  | - |  | Off |  | 82 deg |  | 1,937 ohm | 28 ohm | 28 ohm | 0 |  | 2,905 ohm | 32 ohm | 32 ohm | 0,8 s |  | 28,375 ohm | 35 ohm | 35 ohm | 1,6 s |  |  |  |  | 0 | [7 empty] | Setting Terpasang | [8 empty] | Distance Z2, Z3, Mho Z2, Mho Z3 | On | 0 s |  | Distance Z2, Mho Z2 | Distance Z2, Mho Z2 | On | 0,05 s | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000/1A |  | 0,97 A | 0,44 (SI) | Block | - |  | 0,16 A | 0,71 (SI) | Block | - | - | - | [20 empty] | UITJBB/01/04/2019/257
PHT.37 | GROGOL BARU | GROGOL | https://docs.google.com/spreadsheets/d/1y_KEthuDmKH7Kmw89cyJGkzUkDYIYRAG2VDfff1zLQ8/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000/1A | 150kV/100V |  | 0,016 uF / km | 0,016 uF / km | 0,374 ohm/km | 1,29 / 0,67 | 2 km | 82 |  | On | 0,2 A | 0 | On | 2 A | On |  | On | 10 s |  | - |  | Off |  | 82 deg |  | 0,599 ohm | 28 ohm | 28 ohm | 0 |  | 1,078 ohm | 32 ohm | 32 ohm | 0,4 s |  | 1,796 ohm | 35 ohm | 35 ohm | 1,6 s |  |  |  |  | 0 | [7 empty] | Setting Terpasang | [8 empty] | Distance Z2, Z3, Mho Z2, Mho Z3 | On | 0 |  | Distance Z2, Mho Z2 | Distance Z2, Mho Z2 | On | 0,05 s | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000/1A |  | 0,97 A | 0,44 (SI) | Block | - |  | 0,16 A | 0,71 (SI) | Block | - | - | - | [20 empty] | UITJBB/01/04/2019/256
PHT.38 | GROGOL BARU | GROGOL | https://docs.google.com/spreadsheets/d/1-wcH0elM2bE4HU8pItllVy-RmVCos8WejvdoBYK3p3s/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000/1A | 150kV/100V |  | 0,016 uF / km | 0,016 uF / km | 0,374 ohm/km | 1,29 / 0,67 | 2 km | 82 |  | On | 0,2 A | 0 | On | 2 A | On |  | On | 10 s |  | - |  | Off |  | 82 deg |  | 0,599 ohm | 28 ohm | 28 ohm | 0 |  | 1,078 ohm | 32 ohm | 32 ohm | 0,4 s |  | 1,796 ohm | 35 ohm | 35 ohm | 1,6 s |  |  |  |  | 0 | [7 empty] | Setting Terpasang | [8 empty] | Distance Z2, Z3, Mho Z2, Mho Z3 | On | 0 s |  | Distance Z2, Mho Z2 | Distance Z2, Mho Z2 | On | 0,05 s | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000/1A |  | 0,97 A | 0,44 (SI) | Block | - |  | 0,16 A | 0,71 (SI) | Block | - | - | - | [20 empty] | UITJBB/01/04/2019/256
PHT.39 | KEBON JERUK | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1-rDkfQkizAlX0VLdsvC2PMXvj8PPwlCoVvYlYQu2zVQ/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enable | Disable | Disable | Enable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Enabled | Enabled | Disable |  | Setting Terpasang | -328596 | 150kV/100 V | 5,4 km | 4.275 | 57 deg | 0.64 | -4 |  | 1.5 | 10 A | 30 % | 150 % | 0 | Disable | Disable | Disable | Disable | Disable | Disable | [17 empty] | Disbale |  | MCB Only | I diff + STD | Blocking | [17 empty] | 32 V | 13 | - | - | - | - | - | - | [11 empty] | OCR/GFR | ABB - REF 615 |  | Setting Terpasang | -328596 |  | 4,75 | 0,49 | - | - |  | 0,8 | 0,75 | - | - | - | - | [17 empty] | DKSI/22/10/2021/111
PHT.40 | KEBON JERUK | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1Pbb3-uQViRHekIu8NQJjGnQy3pB8P5rrLUg3yeIKSck/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enable | Disable | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Disable | Disable | Disable | Disable | Disable | Disable | Enabled | Enabled | Disable |  | Setting Terpasang | -328596 | 150kV/100 V | 10.2 | 4.68 | 72 deg | 0.77 | -17 |  | 1,5 A | 10 A | 30 % | 150 % | 0 | Disable | Disable | Disable | Disable | Disable | Disable | [17 empty] | Enable |  | Measured + MCB | I diff + STD | Blocking | [17 empty] | 32 V | 13 | - | - | - | - | - | - | [11 empty] | OCR/GFR | ABB - REF 615 |  | Setting Terpasang | 1000/5 A |  | 5,52 A | 0,459 SI | - | - |  | 0,92 | 0,739 SI | - | - | - | - | [17 empty] | DKSI/22/10/2021/111
PHT.41 | KEBON JERUK | KARET BARU | https://docs.google.com/spreadsheets/d/1iONbCkN9DcoZYBeLDGSiNEIfzUN_qC0vsLU0QL5YHwQ/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enable | Disable | Disable | Enable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Enabled | Disable | Disable |  | Setting Terpasang | 500/5 | 150kV/100 V | 5,4 km | 8.55 | 57 deg | 0.64 | -4 |  | 1.5 | 10 A | 30 % | 150 % | 0 | Disable | Enable | Disable | Disable | Disable | Disable | [17 empty] | Disabled |  | Measured Only | I diff + STD | Blocking | [17 empty] | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | ABB - REF 615 |  | Setting Terpasang | 500/5 |  | 6 | 0.56 | - | - |  | 1 | 0.85 | - | - | - | -
PHT.42 | KEBON JERUK | KARET BARU | https://docs.google.com/spreadsheets/d/106ZFohplNWZhl71Pv_x1VAytkny9X2DfHjhD1ztdd6I/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enable | Disable | Disable | Enable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Enabled | Enabled | Disable |  | Setting Terpasang | 500/5 | 150kV/100 V | 5,4 km | 0.57 | 57 deg | 0.64 | -4 |  | 1.5 | 10 A | 30 % | 150 % | 0 | Disable | Enable | Disable | Disable | Disable | Disable | [17 empty] | Disbale |  | Measured Only | I diff + STD | Blocking | [17 empty] | 32 | 13 | - | - | - | - | - | - | [11 empty] | OCR/GFR | ABB - REF 615 |  | Setting Terpasang | 500/5 |  | 6 | 0.56 | - | - |  | 1 | 0.85 | - | - | - | -
PHT.43 | MUARAKARANG BARU | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1_7up2oXNP8bDecvQ03tANwi9DONnbLG1Jq8Hq0k01Mk/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 2000 / 1 A | 150 kV / 100 V | 0.26 km | 0.05 ohm | 73 deg | 0.72 | -11 deg |  | 0.3 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | MCB Only | Standard | Disabled |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000 / 1 A |  | 1.2 A | 0.41 SI | Disabled | - |  | 0.2 A | 0.74 SI | Disabled | - | Disabled | Disabled
PHT.44 | MUARAKARANG BARU | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1w8RYbap1AWwu9vGJ7EC6uW-rT5GbJ4Dy_KJDob-KKkU/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 2000 / 1 A | 150 kV / 100 V | 0.26 km | 0.05 ohm | 73 deg | 72% | -11 deg |  | 0.3 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | MCB Only | Standard | Disabled |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 2000 / 1 A |  | 1.2 A | 0.41 SI | Disabled | - |  | 0.2 A | 0.74 SI | Disabled | - | Disabled | Disabled
PHT.45 | MUARAKARANG BARU | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1Ies8lAx8df_Hsyo3-E-xiirDcgvhD1hz8ZSWqvG-LgI/edit?usp=drive_link | MICOM P545 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 767011 |  | 0.75 | 0.375 | - | - |  | 0.13 | 0.705 | - | - | - | -
PHT.46 | MUARAKARANG BARU | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1lBiXVwY0r9BSraQc-cDQn3CcjxtoQCIDp5xP2nIIfR8/edit?usp=drive_link | MICOM P545 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | ALSTOM - MICOM P142 |  | Setting Terpasang | 767011 |  | 0.75 | 0.375 | - | - |  | 0.13 | 0.705 | - | - | - | -
PHT.47 | NEW SENAYAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1lGMff0B0Vx_cn1EmcOhgtwmeHA5UJMtK9UNM2Z8YKhU/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Group 1 | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | -328596 | - | 9.87 km | 0.15 ohm | 72.87 deg | 0.772 | -17.234 deg |  | 0.93 A | 9.25 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | - | - | - | - | - |  | MCB Only | Disabled | Blocking |  | 0,12 ohm | 72,87 deg | 4,38 ohm | 0,18 ohm | 72,87 deg | 4,86 ohm | 0,33 ohm | 72,87 deg | 5,41 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | SCHNEIDER - MICOM P123 |  | Setting Terpasang | 1000 / 1 A |  | 1.11 In | 0.4 SI | - | - |  | 0.18 In | 0.725 SI | - | - | No | No
PHT.48 | NEW SENAYAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1uKIjsZbKKW3vINvUVaxo7QdxAKOrLSs1K94710hJecw/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Group 1 | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | -328596 | - | 9.87 km | 0,15 ohm | 72.87 deg | 77.2% | -17.234 deg |  | 0.93 A | 9.25 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | - | - | - | - | - |  | MCB Only | Disabled | Blocking |  | 0,12 ohm | 72,87 deg | 4,38 ohm | 0,18 ohm | 72,87 deg | 4,86 ohm | 0,33 ohm | 72,87 deg | 5,41 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | SCHNEIDER - MICOM P123 |  | Setting Terpasang | 1000 / 1 A |  | 1.11 In | 0.4 SI | - | - |  | 0.18 In | 0.725 SI | - | - | No | No
PHT.49 | NEW SENAYAN | SENAYAN | https://docs.google.com/spreadsheets/d/1DktR8xxYTa8UgieS5NzFt7Qg96EbC4qfY_5b7-gC73I/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000 / 1 A | 150 kV / 100 V | 5 km | 0,12 ohm | 84 deg | 0,72 | -17 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Disabled | - | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 | - |  | Measured + MCB | Disabled | Disabled |  | 0,94 ohm | 84 deg | 33,59 ohm | 1,85 ohm | 84 deg | 41,99 ohm | 3,110 ohm | 84 deg | 52,49 ohm |  | Not Active | [5 empty] | 52 V | 11,5 V | Eb\nabled | V< | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | ALSTOM - MICOM P14DL |  | Setting Terpasang | 2000 / 1 A | Group 1 | 0,66 A | 0,5 SI | Disabled | Disabled | Group 1 | 0,11 A | 0,78 SI | Disabled | Disabled | Disabled | Disabled
PHT.50 | NEW SENAYAN | SENAYAN | https://docs.google.com/spreadsheets/d/15gcmP5VjWWFc3MMiBgZv2QNc3XSUyvcaZkGMF2cYhxI/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000 / 1 A | 150 kV / 100 V | 5 km | 0,12 ohm | 84 deg | 0,72 | -17 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Disabled | - | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 | - |  | Measured + MCB | Disabled | Disabled |  | 0,94 ohm | 84 deg | 33,59 ohm | 1,85 ohm | 84 deg | 41,99 ohm | 3,110 ohm | 84 deg | 52,49 ohm |  | Not Active | [5 empty] | 52 V | 11,5 V | Eb\nabled | V< | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | ALSTOM - MICOM P14DL |  | Setting Terpasang | 2000 / 1 A | Group 1 | 0,55 A | 0,47 SI | Disabled | Disabled | Group 1 | 0,1 A | 0,77 SI | Disabled | Disabled | Disabled | Disabled
PHT.51 | NEW SENAYAN | ULUJAMI | https://docs.google.com/spreadsheets/d/1MC6UbAz2f9O6ayqUHDH_g7iUjPQQI5-IdXThFVgCHns/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/1 A |  | 0,153 ohm | 0,082 ohm | 0,458 ohm | 0,435 ohm | 0,696 ohm | 0,116 ohm | 3,054 km |  | 0,2 A | 1 | 1 | 1 |  | 0.838 | 0.318 | 61 | 0.24 | 0 | 0.24 | 0 | 0.433 | 0.4 | 0.433 | 0.4 | 0.721 | 1.2 | 0.721 | 1.2 | 0.433 | Z1, Z2 and Z3 | PUTT |  |  | Enable | Enable |  |  | Disable | Enable | Disable | Disable | [12 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 2000-01-01 | Group 1 | 0.44 | 0.45 | disabled | disabled | Group 1 | 0.074 | 0.747 | disabled | disabled | ENABLE | disabled
PHT.52 | NEW SENAYAN | ULUJAMI | https://docs.google.com/spreadsheets/d/1-IJaaTiettplWcaFkecHD5zfnswK8b_tCcnH3d7p_eY/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV / 100V | 3.05 | 0.3 ohm | 62 | 0.9 | -21 |  | 0.2 | 2 | 30% | 150% | 0 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0.4 | 1.6 | PUR |  | Disabled |  | Enable Pole Dead | 000011 | Enable | 000011 |  |  | Measured + MCB | I Diff + Std | Blocking |  | 0.24 | 62 | R1 GND 63,45 | 0.43 | 62 | R2 GND 70,49 | 0.72 | 62 | R3 GND 78,33 |  | Disabled |  |  |  |  | DISABLE | [19 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 2000/1 A | Group 1 | 0,44 | 0,45 | Disable | Disable | Group 1 | 0.074 | 0,747 | - | - | - | -
PHT.53 | PANTAI INDAH KAPUK | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1YGa_PVGzABwUO_XdoGaxHbpdee8b9otrhWySIYGOLU0/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 4000/1 A | 150kV/100V | 4.6 km | 15.31 ohm | 81 deg | 0.66 | 5 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | POR | 0.1 s | Disabled |  | Enabled PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) |  |  | Measured + MCB | Disabled |  |  | 12.25 ohm | 81 deg | 28.22 ohm | 18.37 ohm | 81 deg | 35.27 ohm | 26.76 ohm | 81 deg | 44.09 ohm |  | 1PAR/3PAR | BAR 3 PHASE | 1.5 s | 1000 ms |  |  | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.17 Hz | [11 empty] | OCR/GFR | Siemens - 7SJ63 |  | Setting Terpasang | 767011 |  | 0,75 A (sec); 3000 A (pri) | 0.33 (SI) | - | - |  | 0,13 (sec); 520 A (pri) | 0.63 (SI) | - | - | - | - | [17 empty] | TJBB/01/04/2019/153
PHT.54 | PANTAI INDAH KAPUK | DAAN MOGOT | https://docs.google.com/spreadsheets/d/13MdaR73iIKtJX5PAgkQ_ZbBPPp-y9QUKpFXvBcltxLw/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLE | ENABLE | DISABLE | ENABLE | DISABLE | DISABLE | ENABLE | DISABLE | DISABLE | DISABLE | DISABLE | ENABLE | DISABLE | DISABLE | DISABLE | ENABLE | ENABLE | ENABLE |  | Setting Terpasang | 4000/1 A | 150kV / 100V | 4,6 km | 15.31 Ohm | 81 | 0.66 | 5 |  | 0.2 | 2 | 30% | 150% | 0 | [12 empty] | 0s | 0.4s | 1.6s | POR | 20ms | Disable | - | Enable Pole Dead | 000110 (Z2 Z3) | Enable | 000110 (Z2 Z3) | - |  | Measured + MCB | Disable | - |  | 12,25 ohm | 81 deg | 28,22 ohm | 18,37 ohm | 81 deg | 35,27 ohm | 26,76 ohm | 81 deg | 44,09 ohm |  | 1PAR/3PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enable | 15 deg | 6,5 V | 0,17 Hz | [11 empty] | OCR/GFR | Siemens - 7SJ63 |  | Setting Terpasang | 4000/1 A | On | 0,75 A (sec) | 0,33 (Normal Inverse) | - | - | On | 0,13 A (sec) | 0,63 (Normal Inverse) | - | - | - | - | [17 empty] | TJBB/01/04/2019/153
PHT.55 | PANTAI INDAH KAPUK | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1RkCiSNWQAMb88zA5-RuysCadr4crMJJe0rn_5O97PwU/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLE | ENABLE | DISABLE | ENABLE | DISABLE | DISABLE | ENABLE | DISABLE | DISABLE | DISABLE | DISABLE | ENABLE | DISABLE | DISABLE | DISABLE | ENABLE | ENABLE | ENABLE |  | Setting Terpasang | 4000/1 A | 150kV / 100V | 4,93 km | 15,82 Ohm | 81 | 0.66 | 5 deg |  | 0.3 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.8 s | 1.6 s | POR | 100 ms | Disable | - | Enable Pole Dead | 000011 (Z1 Z2) | Enable | 000011 (Z1 Z2) | - |  | Measured + MCB | I DIFF | - |  | 12,66 ohm | 81 deg | - | 18,99 ohm | 81 deg | - | 19.09 ohm | 81 deg | - |  | 1PAR/3PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enable | 15 deg | 6 V | 0,17 Hz | [11 empty] | OCR/GFR | Siemens - 7SJ67 |  | Setting Terpasang | 4000/1 A | On | 0,75 A (sec) | 0,31 (Normal Inverse) | - | - | On | 0,13 A (sec) | 0,57 (Normal Inverse) | - | - | - | - | [17 empty] | DKSI/24/03/2021/80
PHT.56 | PANTAI INDAH KAPUK | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1bzJMnzBNtFfjomWM7ESw7rkW_8ghzQDOzQFbVksZByg/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLE | ENABLE | DISABLE | ENABLE | DISABLE | DISABLE | ENABLE | DISABLE | DISABLE | DISABLE | DISABLE | ENABLE | DISABLE | DISABLE | DISABLE | ENABLE | ENABLE | ENABLE |  | Setting Terpasang | 4000/1 A | 150kV / 100V | 4,93 km | 15,82 Ohm | 81 | 0.66 | 5 deg |  | 0.3 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.8 s | 1.6 s | POR | 100 ms | Disable | - | Enable Pole Dead | 000011 (Z1 Z2) | Enable | 000011 (Z1 Z2) | - |  | Measured + MCB | I DIFF | - |  | 12,66 ohm | 81 deg | - | 18,99 ohm | 81 deg | - | 19.09 ohm | 81 deg | - |  | 1PAR/3PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enable | 15 deg | 6 V | 0,17 Hz | [11 empty] | OCR/GFR | Siemens - 7SJ67 |  | Setting Terpasang | 4000/1A | on | 0.75A | 0.31 | - | - | on | 0.12A | 0.57 s | - | - | - | - | [17 empty] | DKSI/24/03/2021/80
PHT.57 | TOMANG | GROGOL | https://docs.google.com/spreadsheets/d/1HSPLekve4h2FgfFw4r9w23Uh28rpQE0KBO38A1CCU6k/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150 kV/100 V | 4.11 | 0,83 ohm | 85 deg | 0.26 | 26 deg |  | 0.3 A | 2 A | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 | 0.4 s | 1.2 s | - | - | - | - | Enable Pole Dead | (Z2 Z3) | Enable | (Z2 Z3) | - |  | Measured + MCB | Idiff + STD | - |  | 0,66 ohm | 85 | 39 | 1,15 ohm | 85 deg | 43 | 2,38 | 85 | 48 |  |  | - | - | - | - |  | 32 | 13 | - | - | - | - | - | - | [11 empty] | OCR/GFR | EASERGY P142 |  | Setting Terpasang | 2000/1 A |  | 0.72 | 0.4 | Block |  |  | 0.12 | 0.675 | BLOCK |  | - | - | [17 empty] | UITJBB/01/04/2019/
PHT.58 | TOMANG | GROGOL | https://docs.google.com/spreadsheets/d/1fRlcSaCHamkAJa-kLVTsvRPdIe30kqNbHtcWboAD4Vc/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150 kV/100 V | 4.11 | 0.83 ohm | 85 deg | 0,26 | 26 deg |  | 0.3 A | 2 A | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 | 0.4 s | 1.2 s | - | - | - | - | Enable Pole Dead | (Z2 Z3) | Enable | (Z2 Z3) | - |  | Measured + MCB | Idiff + STD | - |  | 0,66 ohm | 85 | 39 | 1,15 ohm | 85 deg | 45 | 2,38 | 85 | 48 |  |  | - | - | - | - |  | 32 | 13 | - | - | - | - | - | - | [11 empty] | OCR/GFR | EASERGY P142 |  | Setting Terpasang | 2000/1 A |  | 0.72 | 0.4 | Block |  |  | 0.12 | 0.675 | BLOCK |  | - | - | [17 empty] | UITJBB/01/04/2019/
PHT.59 | ULUJAMI | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1bG5rOiNz_-liuI3ZWq6e9w0Pvo9SQmXx2tLZR0kWhyU/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/1 A |  | 0,153 ohm | 0,082 ohm | 0,458 ohm | 0,435 ohm | 0,696 ohm | 0,116 ohm | 3,054 km |  | 0,2 A | 1 | 1 | 1 |  | 0.838 | 0.318 | 62 | 0.24 | 0 | 0.24 | 0 | 0.982 | 0.4 | 0.982 | 0.4 | 5.018 | 1.6 | 5.108 | 1.6 | 0.982 | Z1, Z2 and Z3 | PUTT |  |  | Enable | Enable |  |  | Disable | Enable | Disable | Disable | [12 empty] | OCR/GFR | GE Alstom - P14D |  | Setting Terpasang | 2000-01-01 | Group 1 | 0.44 | 0.45 | disabled | disabled | Group 1 | 0.07 | 0.745 | disabled | disabled | disabled | disabled | [12 empty] | TJBB/01/04/2020/149
PHT.60 | ULUJAMI | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1EHa-YQkKZlA61m19012MYQii-qV-p8Ktr5ULbtaWjp0/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV / 100V | 3.05 | 0.3 | 62 | 0.9 | -21 |  | 0.2 | 2 | 30% | 150% | 0 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0.4 | 1.6 | PUR |  | Disabled |  | Enable Pole Dead | 000011 | Enable | 000011 |  |  | Measured + MCB | I Diff + Std | Blocking |  | 0.24 | 62 | R1 GND 63,45 | 0.98 | 62 | R2 GND 70,49 | 5.02 | 62 | R3 GND 78,33 |  | Disabled | [5 empty] | 52 | 11.5 |  | V< and Vdiff> | Enable | 15 | 6 | 0.165 | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 2000/1 A | Group 1 | 0,44 | 0,45 | Disable | Disable | Group 1 | 0,07 | 0,745 | - | - | - | - | [17 empty] | TJBB/01/04/2020/150
PHT.61 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/18zfpWH0vK84CS9EeyuCUVbranP1Onxw7d50n0ZfT2tU/edit?usp=drive_link | RED670 | Setting Terpasang | [45 empty] | Setting Terpasang | [47 empty] | Setting Terpasang | [8 empty] | *OCR: OCR/GFR; I>>: Setting Terpasang
PHT.62 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1oxan4y0FQIZgplW7ic3vnTaZnOW84GFRmO1fF9bNtgE/edit?usp=drive_link | RED670 | Setting Terpasang | [45 empty] | Setting Terpasang | [47 empty] | Setting Terpasang | [8 empty] | *OCR: OCR/GFR; I>>: Setting Terpasang
PHT.63 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1BfK_HajYZX8ks1L6JFY9oCN2m9qPEcjYXpr9qFUzH6c/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.64 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1-MyjOpotSCGEaWnns23yqX-OV3sWSEvkq5-Q2DE-NcA/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.65 | MUARAKARANG BARU | TANJUNG PRIOK |  | RED670 | #N/A
PHT.66 | MUARAKARANG BARU | TANJUNG PRIOK |  | RED670 | #N/A
PHT.67 | MUARAKARANG BARU | TANJUNG PRIOK |  | 7SL87 | #N/A
PHT.68 | MUARAKARANG BARU | TANJUNG PRIOK |  | 7SL87 | #N/A
PHT.69 | CURUG | CIKUPA | https://docs.google.com/spreadsheets/d/1gS4R9JIPm3MxppUtT-afKiselL-PRe9Jkqt5ZeCir5Y/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV/100V | 18,9 km | 2,26 ohm | 81 deg | 0,24 | -123,0 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | IDiff + Std | Blocking |  | 1,809 ohm | 81 deg | 26,09 ohm | 3,160 ohm | 81 deg | 32,61 ohm | 5,989 ohm | 81 deg | 40,77 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V |  | V< | Enabled | 15 deg | 6 V | 165 mHz | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 2000/1 A | Group 1 | 0,85 A | 0,390 (SI) | - | - | Group 1 | 0,14 A | 0,660 (SI) | - | - | - | - | [17 empty] | DKSI/22/01/2020/62
PHT.70 | CURUG | CIKUPA | https://docs.google.com/spreadsheets/d/10XThA6g2zUyrvsbjt9c_Yb3G49qXwNzHaO3q8Fs15UI/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3200/1 A | 150kV/100V | 18,6 km | 3,560 ohm | 81 deg | 0,86 | -31 deg% |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Idiff + Std | Blocking |  | 2,850 ohm | 81 deg | 34,41 ohm | 5,05 ohm | 81 deg | 43,03 ohm | 9,511 ohm | 81 deg | 53,76 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - |  | Enabled | 15 deg | 6 V | 170 mHz | [11 empty] | OCR/GFR | Alstom - Micom P127 |  | Setting Terpasang | 3200/1 A | Group 1 | 0,53 A | 0,425(SI) | - | - | Group 1 | 0,09 A | 0,7(SI) | - | - | - | - | [17 empty] | DKSI/22/01/2020/62
PHT.71 | CURUG | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/158xnn4VUt8rYrAHQ9dc9GJtu1bCtB_Xsf08oSfRmVDM/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3200/1 A | 150kV/100V | 4,7 km | 0,900 ohm | 81 deg | 0,86 | -31 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | - | - | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Idiff + Std | Blocking |  | 0,72 ohm | 81 deg | 50,39 ohm | 1,56 ohm | 81 deg | 56 ohm | 2,649 ohm | 81 deg | 62,21 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Disabled | [14 empty] | OCR/GFR | Alstom - Micom P127 |  | Setting Terpasang | 3200/1 A | Group 1 | 0,54 A | 0,4(SI) | - | - | Group 1 | 0,093 A | 0,675(SI) | - | - | - | - | [17 empty] | DKSI/22/01/2020/62
PHT.72 | CURUG | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/1y0BlikOs-AdK9euUH0YZjzEqA0eL3gT_xEwtq64uPRU/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV/100V | 4,7 km | 0,570 ohm | 81 deg | 0,86 | 81 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | - | - | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Idiff + Std | Blocking |  | 0,45 ohm | 81 deg | 31,49 ohm | 0,97 ohm | 81 deg | 34,98 ohm | 1,649 ohn | 81 deg | 38,88 |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 2000/1 A | Group 1 | 0,87 A | 0,41(SI) | - | - | Group 1 | 0,14 A | 0,685(SI) | - | - | - | - | [17 empty] | UITJBB/01/04/2019/165
PHT.73 | GAJAH TUNGGAL | PASAR KEMIS | https://docs.google.com/spreadsheets/d/15M9aJzZzNu5hlgrMke4A-x8s0Bqc0Sw3YQzyredDJcI/edit?usp=drive_link | L90 | Setting Terpasang |  | 2000 / 1 A | 150 kV / 100 V |  |  |  | 0.3 pu | [11 empty] | 1.77 ohm | 82 deg | [7 empty] | 0 s |  | 3.42 ohm | 82 deg | [7 empty] | 0.4 s | [5 empty] | Setting Terpasang |  | 5.75 ohm | 82 deg | [7 empty] | 1.6 s | [38 empty] | Setting Terpasang | [39 empty] | OCR/GFR | ABB - REF615 | Setting Terpasang | 2000 / 1 A |  | 0.97 A | 0.337 SI | Disabled | Disabled |  | 0.162 A | 0.586 SI | Disabled | Disabled
PHT.74 | GAJAH TUNGGAL | PASAR KEMIS BARU | https://docs.google.com/spreadsheets/d/1kC70sE5aQrIpuxGujxYvzZvZXsJUypCKBD4qR5Hbgcc/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 2000 / 1 A | 150 kV / 100 V | 6.6 km | 1.85 ohm | 82 deg | 0.64 | -11 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | [14 empty] | 1.48 ohm | 82 deg |  | 2.33 ohm | 82 deg |  | 3.81 ohm | 82 deg |  |  | 1PAR/3PAR |  |  | 1 s | 3 s | [20 empty] | OCR/GFR | ABB - REF615 |  | Setting Terpasang | 2000 / 1 A |  | 0.97 A | 0.35 SI | Disabled | Disabled |  | 0.16 A | 0.64 SI | Disabled | Disabled
PHT.75 | ITS | TANGERANG BARU | https://docs.google.com/spreadsheets/d/183f3r1m0S_cQEntotSm-DMYWR7td4P67IJDiI6E5k9U/edit?usp=sharing | MICOM P545 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | SIEMENS - 7SJ82 |  | Setting Terpasang
PHT.76 | ITS | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1aqNg3Mlr9twgz_hGmVOGxUwz9HbewC6tlkYDjQsfu9g/edit?usp=drive_link | MICOM P543 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | SIEMENS - 7SJ82 |  | Setting Terpasang | 767011 |  | 0.95 | 0.234 | - | - |  | 0.158 | 0.486 | - | - | - | -
PHT.77 | ITS | KONSUMEN | https://docs.google.com/spreadsheets/d/1DSkWdSbfURDayk9UcU3AzxdzyZQ16FUv2rJ1ux90TLE/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | SIEMENS - 7SJ82 |  | Setting Terpasang
PHT.78 | JATAKE | CIKUPA | https://docs.google.com/spreadsheets/d/19rEhayqjtwaWSoT5ZTvIbc5k2NzuDDs1Laia6Fj-Nsc/edit?usp=drive_link | MICOM P442 | Setting Terpasang | [20 empty] | Setting Terpasang | [76 empty] | OCR/GFR | ABB - REF615 |  | Setting Terpasang | 2000-05-01 |  | 4.675 A | 0.36 SI | - | - |  | 0.78 A | 0.62 SI | - | - | Disabled | Disabled
PHT.79 | JATAKE | CIKUPA | https://docs.google.com/spreadsheets/d/1vzC1yp74fxeW_SkTib1X3vUtPqKeRIPe4QzDFGSWtYE/edit?usp=drive_link | MICOM P442 | Setting Terpasang | [20 empty] | Setting Terpasang | [76 empty] | OCR/GFR | Schneider - Micom P142 |  | Setting Terpasang | -109450 |  | 6 A | 0,375 SI | - | - |  | 1 A | 0,635 SI | - | - | - | -
PHT.80 | JATAKE | JATAKE BARU | https://docs.google.com/spreadsheets/d/1JeQl8fuBX8efnvZ36FsRC3KOBPdukfNMtC4OZXnd90s/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/5 A |  | 0,234 ohm | 0,032 ohm | 0,701 ohm | 0,157 ohm | 0 | 0 | 3,12 km |  | 1 | 1 | 1 | 0 |  | 0,678 ohm | -0,085 ohm | 82 deg | 0,189 ohm | 0 s | 0,189 ohm | 0 s | 0,497 ohm | 0,4 s | 0,497 ohm | 0,4 s | 1,127 ohm | 1,6 s | 1,127 ohm | 1,6 s | 0,497 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | Schneider - Micom P123 |  | Setting Terpasang | 1600/5A |  | 6 A | 0,394 (SI) | - | - |  | 1 A | 0,66 (SI) | - | - | - | - | [12 empty] | TJBB/01/04/2021/37
PHT.81 | JATAKE | JATAKE BARU | https://docs.google.com/spreadsheets/d/1U4LNFfdRgkG3oTL8LS9vYsoJSOwmdYIxb6iZucimlf8/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/5A |  | 0,234 ohm | 0,032 ohm | 0,701 ohm | 0,157 ohm |  | - | 3,12 km |  | 1 | 1 | 1 | 0 |  | 0.678 | -0.085 | 82 | 0.189 | 0 | 0.189 | 0 | 0.497 | 0.4 | 0.497 | 0.4 | 1.127 | 1.6 | 1.127 | 1.6 | 0.497 | Z2 and Z3 | POTT |  | Disable | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | Schneider - Micom P123 |  | Setting Terpasang | 2000-05-01 |  | 4.85 A | 0,354 (SI) | - | - |  | 0.825 | 0,609 (SI) | - | - | - | - | [12 empty] | TJBB/01/04/2021/37
PHT.82 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/15GsUKUcg8JFZFdO28Po0aIH7dQZTMd49pg75AzRjtqc/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 1000/1A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm |  |  | 0,99 km |  | 0,2 | 1 | 1 | 1 |  | 0.809 | -0.169 | 86 deg | [37 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000/1A | 50/51P3 | 1,2 A (sec) | 0.427 | - | - | 50/51G4 | 0.184 | 0.7 | - | - | - | - | [12 empty] | TJBB/01/04/2018/170
PHT.83 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1Aq7yTz8ADrd9gs4q9_ofm_8Fmb-bD8-uFGXMHXiPROk/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 1000/1A |  | 0,08 ohm | 0,025 ohm | 0,241 ohm | 0,135 ohm | - | - | 1,1 km |  | 0,2 ohm | 1 | 1 | 1 |  | 0.761 | -0.229 | 73 deg | 0,067 ohm | 0 s | 0,067 ohm | 0 s | 0,121 ohm | 0,4 s | 0,121 ohm | 0,4 s | 0,202 ohm | 1,6 s | 0,202 ohm | 1,6 s | 0,067 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000/1A | 50/51P3 | 1,2 A (sec) | 0,405(SI) | - | - | 50/51G4 | 0,2 A (sec) | 0,669(SI) | - | - | - | - | [12 empty] | TJBB/01/04/2018/170
PHT.84 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/15GsUKUcg8JFZFdO28Po0aIH7dQZTMd49pg75AzRjtqc/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 1000/1A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm |  |  | 0,99 km |  | 0,2 | 1 | 1 | 1 |  | 0.809 | -0.169 | 86 deg | [37 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000/1A | 50/51P3 | 1,2 A (sec) | 0.427 | - | - | 50/51G4 | 0.184 | 0.7 | - | - | - | - | [12 empty] | TJBB/01/04/2018/170
PHT.85 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1Aq7yTz8ADrd9gs4q9_ofm_8Fmb-bD8-uFGXMHXiPROk/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 1000/1A |  | 0,08 ohm | 0,025 ohm | 0,241 ohm | 0,135 ohm | - | - | 1,1 km |  | 0,2 ohm | 1 | 1 | 1 |  | 0.761 | -0.229 | 73 deg | 0,067 ohm | 0 s | 0,067 ohm | 0 s | 0,121 ohm | 0,4 s | 0,121 ohm | 0,4 s | 0,202 ohm | 1,6 s | 0,202 ohm | 1,6 s | 0,067 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000/1A | 50/51P3 | 1,2 A (sec) | 0,405(SI) | - | - | 50/51G4 | 0,2 A (sec) | 0,669(SI) | - | - | - | - | [12 empty] | TJBB/01/04/2018/170
PHT.86 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/11n1GJXlqbL-fua2lnF0pUvVF-UHI58wZnqL0wpwUnJE/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150 kV / 100 V | 1000 / 1 A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,2 A | 1 | 1 | 1 |  | 0,7 | 174 | 83 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000 / 1 A |  | 1,2 | 0.123 | - | - |  | 0.184 | 0.69
PHT.87 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/1Y0-J-8ad6pziDYgoE37bzaxqgoc9kqSEsFjNgaD3L7A/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150 kV / 100 V | 1000 / 1 A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,2 A | 1 | 1 | 1 |  | 0,7 | 0.174 | 83 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000 / 1 A |  | 1.1 | 0.436 | - | - |  | 0.184 | 0.69 | - | - | - | -
PHT.88 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/11n1GJXlqbL-fua2lnF0pUvVF-UHI58wZnqL0wpwUnJE/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150 kV / 100 V | 1000 / 1 A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,2 A | 1 | 1 | 1 |  | 0,7 | 174 | 83 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000 / 1 A |  | 1,2 | 0.123 | - | - |  | 0.184 | 0.69
PHT.89 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/1Y0-J-8ad6pziDYgoE37bzaxqgoc9kqSEsFjNgaD3L7A/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150 kV / 100 V | 1000 / 1 A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,2 A | 1 | 1 | 1 |  | 0,7 | 0.174 | 83 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 1000 / 1 A |  | 1.1 | 0.436 | - | - |  | 0.184 | 0.69 | - | - | - | -
PHT.90 | SINDANG JAYA | BALARAJA | https://docs.google.com/spreadsheets/d/1IK2DYZcHm5MkukKyo1x7sG4osnO77byJ3aebcjgBbsQ/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 4000/1A |  | 3,339 ohm | 0,426 ohm | 10,016 ohm | 2,202 ohm | - | - | 7,69 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 83 deg | 4,664 ohm | 0 s | 4,664 ohm | 0 s | 7,956 ohm | 0,4 s | 7,956 ohm | 0,4 s | 17,278 ohm | 1,6 s | 17,278 ohm | 1,6 s | 7.956 ohm | Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Disable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) |  |  | 50/51G4 | 0,137 A (sec) | 0,625(SI) | [16 empty] | TJBB/01/04/2020/64
PHT.91 | SINDANG JAYA | BALARAJA | https://docs.google.com/spreadsheets/d/15gdVi4iRgc364cz2LCPXPoymgaYb-bXkYVqk5pMWfhs/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 4000/1A |  | 3,339 ohm | 0,426 ohm | 10,016 ohm | 2,202 ohm | - | - | 7,69 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 83 deg | 4,664 ohm | 0 s | 4,664 ohm | 0 s | 7,956 ohm | 0,4 s | 7,956 ohm | 0,4 s | 17,278 ohm | 1,6 s | 17,278 ohm | 1,6 s | 7,956 ohm | Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) |  |  | 50/51G4 | 0,137 A (sec) | 0,625(SI) | [16 empty] | TJBB/01/04/2020/64
PHT.92 | SINDANG JAYA | LONTAR | https://docs.google.com/spreadsheets/d/1U-e69FkdoUL2MHWdFa_2hYYwWbYENik7Czn_T0sXlm8/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 4000/1A |  | 9,36 ohm | 1,275 ohm | 28,079 ohm | 6,307 ohm | 9,937 ohm | 1,654 ohm | 12,58 km | [6 empty] | 0.68 | - 0,087 ohm | 82 deg | 7,557 ohm | 0 s | 7,557 ohm | 0 s | 19,917 ohm | 0,4 s | 19,917 ohm | 0,4 s | 37,368 ohm | 1,6 s | 37,368 ohm | 1,6 s | 19,917 ohm | Z1, Z2 and Z3 | PUTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 4000/1A | 50/51P3 | 0,82 A (sec) | 0,374(SI) |  |  | 50/51G3 | 0,137 A (sec) | 0,65(SI) | [16 empty] | UITJBB/01/04/2020/159
PHT.93 | SINDANG JAYA | LONTAR | https://docs.google.com/spreadsheets/d/1qwiSHMFlcv5bowRY0YFSepceEHpXtH9gAImbRim5Et4/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 4000/1A |  | 9,36 ohm | 1,275 ohm | 28,079 ohm | 6,307 ohm | 9,937 ohm | 1,654 ohm | 12,58 km | [6 empty] | 0.68 | - 0,087 ohm | 82 deg | 7,557 ohm | 0 s | 7,557 ohm | 0 s | 19,917 ohm | 0,4 s | 19,917 ohm | 0,4 s | 37,368 ohm | 1,6 s | 37,368 ohm | 1,6 s | 19,917 ohm | Z2 and Z3 | PUTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 4000/1A | 50/51P3 | 0,82 A (sec) | 0,374(SI) |  |  | 50/51G3 | 0,137 A (sec) | 0,65(SI) | [16 empty] | UITJBB/01/04/2020/159
PHT.94 | SINDANG JAYA | SUVARNA SUTERA | https://docs.google.com/spreadsheets/d/1O4iMK9fq5D-Ra0BlxdvdxrAQVSVgmVroY1RpVxIVvxk/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 4000/1A |  | 1,98 ohm | 0,253 ohm | 5,939 ohm | 1,306 ohm | - | - | 4,56 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 83 deg | 2,776 ohm | 0 s | 2,776 ohm | 0 s | 5,628 ohm | 0,4 s | 5,628 ohm | 0,4 s | 9,516 ohm | 1,2 s | 9,516 ohm | 1,2 s | 5628 | Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) |  |  | 50/51G4 | 0,137 A (sec) | 0,625(SI) | [16 empty] | TJBB/01/04/2020/63
PHT.95 | SINDANG JAYA | SUVARNA SUTERA | https://docs.google.com/spreadsheets/d/1zgS9FZQl2jleL4mQE63ZxZbLXZjVl3s33lWSd_btP9I/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 4000/1A |  | 1,98 ohm | 0,253 ohm | 5,939 ohm | 1,306 ohm | - | - | 4,56 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 83 deg | 2,776 ohm | 0 s | 2,776 ohm | 0 s | 5,628 ohm | 0,4 s | 5,628 ohm | 0,4 s | 9,516 ohm | 1,2 s | 9,516 ohm | 1,2 s | 5628 | Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) |  |  | 50/51G4 | 0,137 A (sec) | 0,625(SI) | [16 empty] | TJBB/01/04/2020/63
PHT.96 | TANGERANG BARU | LONTAR | https://docs.google.com/spreadsheets/d/1DThmS_TVshKSUqPXvHlRCDS8SSllAv9njZSdiiIxYzA/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enable | Enable | Disable | Enable | disable | Disable | Enable | Disable | Disable | Disable | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3000/1A | 150kV/100V | 21,22 km | 11,28 ohm | 76 | 670 | -2 deg |  | 0,2 x in | 2 In | 30% | 150% | 0 S | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | I Diff + standart | - |  | 9,030 ohm | 76 deg | 35,32 ohm | 14,14 ohm | 76 deg | 39,25 ohm | 21,53 ohm | 76 deg | 49,06 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Disable | - | - | - | [11 empty] | OCR/GFR | Areva - Micom P141 |  | Setting Terpasang | 3000/1A |  | 1,090 A | 0,3 S | - | - |  | 0,18 A | 0,56 S | - | - | - | Enable | [17 empty] | TJBB/01/04/2023/103
PHT.97 | TANGERANG BARU | LONTAR | https://docs.google.com/spreadsheets/d/1XrLp-G8k7jH4zGHSxyHG0NR2ILCmpE7qbBrtiIPAO50/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3000/1 A | 150kV/100V | 21,28 km | 11,28 ohm | 76 deg | 0,67 | -2 deg |  | 0,2 xIn | 2 xIn | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | I Diff + standart | - |  | 9,03 ohm | 76 deg | 35,32 ohm | 14,14 ohm | 76 deg | 39,25 ohm | 21,53 ohm | 76 deg | 49,06 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Disable | - | - | - | [11 empty] | OCR/GFR | Areva - Micom P141 |  | Setting Terpasang | 3000/1 A |  | 1,090 A | 0,3 S | - | - |  | 0,18 A | 0,56 S | - | - | - | enable | [17 empty] | TJBB/01/04/2023/103
PHT.98 | TANGERANG BARU | ITS | https://docs.google.com/spreadsheets/d/1it9FF1xe83IbwSASHWr6oaErJsEriRUqQaS56v-8wJI/edit?usp=sharing | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 401769 | 150 kV/100V | 2,45 ohm | 3,15 ohm | 87 deg | 0,67 | -4 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | IDiff + Std | Blocking |  | 2,52 ohm | 87 deg | 23,65 ohm | 5,82 ohm | 87 deg | 29,56 ohm | 9,97 ohm | 87 deg | 36,95 ohm |  | Not Active | [5 empty] | 52 V | 11,5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | AREVA - MICOM P141 |  | Setting Terpasang | 401769 |  | 1.2 A | 0.222 SI | - | - |  | 0.2 A | 0.469 SI | - | - | - | -
PHT.99 | TANGERANG BARU | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1j9UPZUhHwjANqFfmzKGm3xEdGXc1O7eyNWCa34mR_Ho/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 3000/1 A | 150kV/100V | 6,5 km | 8,250 km | 87 deg | 0,67 | -4 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 6,6 ohm | 87 deg | 22,14 ohm | 9,9 ohm | 87 deg | 24,6 ohm | 12,47 ohm | 87 deg | 27,34 ohm |  | 1PAR/3PAR | BAR 2 and 3 ph | 500 ms | 1 s | 3 s |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 0,17 Hz | [11 empty] | OCR/GFR | Areva - Micom P141 |  | Setting Terpasang | 3000/1 A |  | 0,96 A | 0,295 S | - | - |  | 0,240 A | 0,5 S | - | - | Disable | Enable | [17 empty] | TJBB/01/04/2017/
PHT.100 | TELUK NAGA | DADAP | https://docs.google.com/spreadsheets/d/1YIxxO10MIvc8tyb1gtdpGEiZdlhWW1RuxusmJ2kgMWk/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3000 / 1 A | 150 kV / 100 V | 6.13 km | 3.490 ohm | 83 deg | 0.68 | -8 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | -% | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 | - |  | Measured + MCB | I Diff + Std | Blocking |  | 2.790 ohm | 83 deg | 25.70 ohm | 12.10 ohm | 83 deg | 28.55 ohm | 21.64 ohm | 83 deg | 31.72 ohm |  | Not Active | - | - | - | - |  | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | Alstom - Micom P141 |  | Setting Terpasang | 3000 / 1 A |  | 1.2 A | 0.275 SI | - | - |  | 0.2 A | 0.525 SI | - | - | Disabled | Disabled
PHT.101 | TELUK NAGA | DADAP | https://docs.google.com/spreadsheets/d/1z7IEr0_A4Qi-QOKuYJdiDxj_6tXWqtlKbaN-WPlrQSc/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3000 / 1 A | 150 kV / 100 V | 6.13 km | 3.490 ohm | 83 deg | 0.68 | -8 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | -% | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 | - |  | Measured + MCB | I Diff + Std | Blocking |  | 2.790 ohm | 83 deg | 25.70 ohm | 12.10 ohm | 83 deg | 28.55 ohm | 21.64 ohm | 83 deg | 31.72 ohm |  | Not Active | - | - | - | - |  | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | Alstom - Micom P141 |  | Setting Terpasang | 3000 / 1 A |  | 1.2 A | 0.275 SI | - | - |  | 0.2 A | 0.525 SI | - | - | Disabled | Disabled
PHT.102 | TELUK NAGA | SEPATAN | https://docs.google.com/spreadsheets/d/1ktTfifoI-vKO265I_tJpjGjERcLVVWM0vTqYn7dHHz0/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | -109571 | 150kV/100V | 9,17 km | 2,77 ohm | 82,15 deg | 0.685 | -7.244 deg |  | 0,2 A | 2 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,8 s | 1,2 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 2,22 ohm | 82,15 deg | 20,25 ohm | 3,32 ohm | 82,15 deg | 22,5 ohm | 4,52 ohm | 82,15 deg | 25 ohm |  | 1PAR/3PAR | BAR 3 Phase | 0,9 s | 1 | 3 |  | 31,75 V | 11,55 V | Enabled | V< V> and Vdiff> | Enabled | 15 deg | 5,77 V | 0,17 Hz | [11 empty] | OCR/GFR | Schneider P142 |  | Setting Terpasang | 1600/1 A |  | 1,2 A (sec) | 0,250 (SI) | - | - |  | 0,2 A (sec) | 0,450 (SI) | - | - | - | -
PHT.103 | TELUK NAGA | SEPATAN | https://docs.google.com/spreadsheets/d/1yDYsqFIpydB6CDBSYEp9OYWIaUX7Qsm0ROMrl7QLxuE/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | -109571 | 150kV/100V | 9,17 km | 2,77 ohm | 82,15 deg | 0.685 | -7.244 deg |  | 0,2 A | 2 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,8 s | 1,2 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 2,22 ohm | 82,15 deg | 20,25 ohm | 3,32 ohm | 82,15 deg | 22,5 ohm | 4,52 ohm | 82,15 deg | 25 ohm |  | 1PAR/3PAR | BAR 3 Phase | 0,9 s | 1 | 3 |  | 31,75 V | 11,55 V | Enabled | V< V> and Vdiff> | Enabled | 15 deg | 5,77 V | 0,17 Hz | [11 empty] | OCR/GFR | Schneider P142 |  | Setting Terpasang | 1600/1 A |  | 1,2 A (sec) | 0,250 (SI) | - | - |  | 0,2 A (sec) | 0,450 (SI) | - | - | - | -
PHT.104 | JATAKE BARU | JATAKE | https://docs.google.com/spreadsheets/d/13ZV4tc5EeW_qFPs7NnfQ2SjrrN8e_QqBhLSaJPdzk6g/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/1A |  | 1,168 ohm | 0,161 ohm | 3,503 ohm | 0,785 ohm | 0 | 0 | 3,12 km |  | 0,2 A | 1 | 1 | 0 |  | 0,682 ohm | -0,085 ohm | 82 deg | 0,943 ohm | 0 s | 0,943 ohm | 0 s | 1,415 ohm | 0,8 s | 1,415 ohm | 0,8 s | 4,688 ohm | 1,6 s | 4,688 ohm | 1,6 s | 1,415 ohm | Z1, Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 2000/1A | 50/51P4 | 0,972 A | 0,374(SI) | - | - | 50/51G4 | 0,162 A | 0,636(SI) | - | - | - | - | [12 empty] | TJBB/01/04/2021/36
PHT.105 | JATAKE BARU | JATAKE | https://docs.google.com/spreadsheets/d/1lBAwbE9vWR6-QkBtTryO638VTZndtaM_wGX5y9820pQ/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/1A |  | 1,168 ohm | 0,161 ohm | 3,503 ohm | 0,785 ohm | 0 | 0 | 3,12 km |  | 0,2 A | 1 | 1 | 0 |  | 0,678 ohm | -0,085 ohm | 82 deg | 0,943 ohm | 0 s | 0,943 ohm | 0 s | 1,415 ohm | 0,8 s | 1,415 ohm | 0,8 s | 4,688 ohm | 1,6 s | 4,688 ohm | 1,6 s | 1,415 ohm | Z1, Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 2000/1A | 50/51P4 | 0,972 A | 0,374(SI) | - | - | 50/51G4 | 0,162 A | 0,636(SI) | - | - | - | - | [12 empty] | TJBB/01/04/2021/36
PHT.106 | JATAKE BARU | TANGERANG | https://docs.google.com/spreadsheets/d/1HFvkvO46ebK0mXTuH1HXRgQR220W2IwVUMjfwdwWwC0/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/1A |  | 2,571 ohm | 0,354 ohm | 7,714 ohm | 1,728 ohm | 33,966 ohm | 11731 | 6,87 km |  | 0,2 A | 1 | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82 deg | 2,076 ohm | 0 s | 2,076 ohm | 0 s | 7,348 ohm | 0,4 s | 7,348 ohm | 0,4 s | 12,998 ohm | 1,6 s | 12,998 ohm | 1,6 s | 7,348 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 2000/1A | 50/51P4 | 0,972 A | 0,374(SI) | - | - | 50/51G4 | 0,164 A | 0,636(SI) | - | - | - | - | [12 empty] | TJBB/01/04/2021/34
PHT.107 | JATAKE BARU | TANGERANG | https://docs.google.com/spreadsheets/d/1c5pCIMYCr_m4Ih5QsIqFUlh0E-R6Xkney5ZWW5CibeA/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/1A |  | 2,571 ohm | 0,354 ohm | 7,714 ohm | 1,728 ohm | 33,966 ohm | 11,731 ohm | 6,87 km |  | 0,2 A | 1 | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82 deg | 2,076 ohm | 0 s | 2,076 ohm | 0 s | 7,348 ohm | 0,4 s | 7,348 ohm | 0,4 s | 12,998 ohm | 1,6 s | 12,998 ohm | 1,6 s | 7,348 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [10 empty] | OCR/GFR | NR - PCS 9611 |  | Setting Terpasang | 2000/1A | 50/51P4 | 0,972 A | 0,374(SI) | - | - | 50/51G4 | 0,164 A | 0,636(SI) | - | - | - | - | [12 empty] | TJBB/01/04/2021/34
PHT.108 | LONTAR | SINDANG JAYA | https://docs.google.com/spreadsheets/d/1Mad--6xOYKdlWz7byYqWgJJ2U-IDHngdf14uvAKoHyk/edit?usp=drive_link | MICOM P443 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 4000/1A | 150kV/100V |  | 12.58 km | 9.446 ohm | 82.2 deg | 0.68 | -7.29 deg | 7.56 ohm | 23,21 ohm | 23,21 ohm | 0 s | 11.34 ohm | 33,16 ohm | 33,16 ohm | 0.4 s | 18.33 ohm | 47,37 ohm | 47,37 ohm | 1.6 s | [6 empty] | PUR | 0 s |  |  | Enabled PoleDead | 30 s | Disabled | Blocking |  |  |  |  | Measured + MCB | Enabled |  | Not Active | [7 empty] | 17.3 V | 46.2 V | 17.3 V | 46.2 V | 5.774 V | 0.5 Hz | 30 deg | [20 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 4000/1 A | Group 1 | 0.82 A | 0.345 SI | - | - | Group 1 | 0.14 A | 0.64 SI | - | -
PHT.109 | LONTAR | SINDANG JAYA | https://docs.google.com/spreadsheets/d/1r7qBDETtEcGGFVwKJvmQXfFoCOcMy-x_xN0dXZsT5MY/edit?usp=drive_link | MICOM P443 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 4000/1A | 150kV/100V |  | 12.58 km | 9.446 ohm | 82.2 deg | 0.68 | -7.29 deg | 7.56 ohm | 23,21 ohm | 23,21 ohm | 0 s | 11.34 ohm | 33,16 ohm | 33,16 ohm | 0.4 s | 18.33 ohm | 47,37 ohm | 47,37 ohm | 1.6 s | [6 empty] | PUR | 0 s |  |  | Enabled PoleDead | 30 s | Disabled | Blocking |  |  |  |  | Measured + MCB | Enabled |  | Not Active | [7 empty] | 17.3 V | 46.2 V | 17.3 V | 46.2 V | 5.774 V | 0.5 Hz | 30 deg | [20 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 4000/1 A | Group 1 | 0.82 A | 0.345 SI | - | - | Group 1 | 0.14 A | 0.64 SI | - | -
PHT.110 | LONTAR | DADAP | https://docs.google.com/spreadsheets/d/1_n9Zp7Y2NoT_qqHqUVK3QLyxdX4QlC3zjlX8DHlFcy0/edit?usp=drive_link | MICOM P446 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 3000 / 1 A | 150 kV / 100 V |  | 26.26 km | 14.94 ohm | 83 deg | 0.68 | -8 deg | 11.95 ohm | 25.70 ohm | 25.70 ohm | 0 s | 17.93 ohm | 28.55 ohm | 28.55 ohm | 0.4 s | 22.11 ohm | 31.72 ohm | 31.72 ohm | 1.6 s | [5 empty] | - | PUR | 0 s | - | - | Enabled PoleDead | 30 s | Disabled | - | - | - | - |  | Measured + MCB | Disabled |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | - | [20 empty] | OCR/GFR | GE - MICOM P141 |  | Setting Terpasang
PHT.111 | LONTAR | DADAP | https://docs.google.com/spreadsheets/d/16N_hQUDTAm-C31zmw9FvHAx4H116toI10NQHsNfMECA/edit?usp=drive_link | MICOM P446 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 3000 / 1 A | 150 kV / 100 V |  | 26.26 km | 14.94 ohm | 83 deg | 68% | -8 deg | 11.95 ohm | 25.70 ohm | 25.70 ohm | 0 s | 17.93 ohm | 28.55 ohm | 28.55 ohm | 0.4 s | 22.11 ohm | 31.72 ohm | 31.72 ohm | 1,6 s | [5 empty] | - | PUR | 0 s | - | - | Enabled PoleDead | 30 s | Disabled | - | - | - | - |  | Measured + MCB | Disabled |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | - | [20 empty] | OCR/GFR | GE - MICOM P141 |  | Setting Terpasang
PHT.112 | LONTAR | TANGERANG BARU | https://docs.google.com/spreadsheets/d/1GK01xt7hoqWLkwpSKVVMm3hH1gWFgjsGNpxPWiTE3es/edit?usp=drive_link | MICOM P546 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 401769 |  | 1.059 | 0.362 |  |  |  | 0.177 | 0.677 | - | - | - | -
PHT.113 | LONTAR | TANGERANG BARU | https://docs.google.com/spreadsheets/d/16vozHIoxHVT0qgs6hajKPjl1Z7aNoJy71doFQVnw1co/edit?usp=drive_link | MICOM P546 | Setting Terpasang | [20 empty] | Setting Terpasang | [77 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang
PHT.114 | CENGKARENG | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1Ww0Df6e_JdVjjcwy_b2eezckHonTWQ-IdRlbOe5HyMI/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 2000/5 A | 150/100 | 10,32 | 1.272 | 84 | 0,67% | -4% |  | 1 | 10 | 30 | 150 | 0 | - | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0,8 | 1,6 | PUR | -% | Disbaled | -% | Enable PoleDead | 00000011 | Enable | 00000011 | -% |  | Measure+MCB | Idiff+std | Blocking |  | 1,018 ohm | 84 | 5,81 | 1,528 ohm | 84 | 6,45 | 2,7 ohm | 84 | 7,17 |  | 1PAR/3PAR | BAR 3 phase | 100 ms | 1 | 3 |  | 52 | 11,5 | - | V< | Enabled | 15 | 6 | 0,165 | [11 empty] | OCR/GFR | Schneider - Micom P122 |  | Setting Terpasang | [30 empty] | TJBB/01/05/2022/70
PHT.115 | CENGKARENG | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1QUT6oi3kKdCYExcT1xM-NcNSsZ0oFRc9vPIlOoAwGZA/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disbaled | Enabled | Disbaled | Disbaled | Enabled | Disbaled | Disbaled | Disbaled | Disbaled | Enabled | Disbaled | Disbaled | Disbaled | Enabled | Enabled | Enabled |  | Setting Terpasang | 2000/5 A | 150/100 | 10,32 | 1.272 | 84 | 0,67% | -4% |  | 1 | 10 | 30 | 150 | 0 | - | - | -% | -% | -% | - | [6 empty] | 0 | 0,8 | 1,6 | PUR | -% | Disabled | -% | Enable Poledead | 0000000011 | Enabled | 0000000011 | -% |  | Measured+MCB | Idiff+Std | Blocking |  | 1,018 ohm | 84 | 5,81 | 1,528 ohm | 84 | 6,45 | 2,7 ohm | 84 | 7,17 |  | 1PAR/3PAR | BAR 3 PHASE | 100 | 1 | 3 |  | 52 | 11,5 | - | V< | Enabled | 15 | 6 | 165 | [11 empty] | OCR/GFR | Schneider - Micom P122 |  | Setting Terpasang | 2000/5 A | Group 1 | 4,8 A | 0,34 | - | - | Group 1 | 0,8 A | 0,591 (SI) | - | - | - | - | [17 empty] | TJBB/01/05/2022/70
PHT.116 | CENGKARENG | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/13dqZROd78XDCm2sGvj4Xk-DGTIpsIokV60v4XNI-RxI/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 767132 | 150/100 | 0,4 | 0.66 | 89 | 0,69% | -12% |  | 1 | 10 | 30 | 150 | 0 | - | - | -% | -% | -% | - | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | Measured+MCB | Idiff+STd | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 | 11,5 | - | V< | Enabled | 15 | 6 | 170 | [11 empty] | OCR/GFR | Areva - Micom P141 |  | Setting Terpasang | CT: 767132; I>: 4,75; tms: 0,23; I>: 0,8; tms: 0,48 | [19 empty] | DKSI/12/05/2022/031
PHT.117 | CENGKARENG | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1JZKV5Er1VvbzG3V4qGwYW__IxmqcaY9PcJlYJ3nx0dU/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3000/5 a | 150/100 | 0,4 | 0.124 | 89 | 0,68% | -12% |  | 1 | 10 | 30 | 150 | 0 | - | - | -% | -% | -% | - | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | Measured+MCB | Idiff+Std | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 | 11,5 | - | V< | Enabled | 15 | 6 | 170 | [11 empty] | OCR/GFR | Areva - Micom P141 |  | Setting Terpasang | CT: 3000/5 A; I>: 6; tms: 0,22; I>: 1; tms: 0,47 | [19 empty] | DKSI/12/05/2022/031
PHT.118 | CENGKARENG | TANGERANG | https://docs.google.com/spreadsheets/d/1hMhfYciYCyp6nppuMwlWI0AgiOB2ycLbQyc1toMrvVA/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000-05-01 | 150kV/100V |  | 0,016 | 0,016 | 0,06 | 1,29/0,67 | 9,23 | 82 |  | on | 1 | 0 | on | 10 | on |  | on | 10 |  | off |  | off |  | 82 |  | 0,949 | 5,502 | 5,502 | 0 |  | 1,424 | 10,881 | 10,881 | 0,4 |  | 2,041 | 10,994 | 10,944 | 1,6 |  | 0,96 |  |  | 0 |  | 1,440 | [5 empty] | Setting Terpasang |  |  |  | 2063 |  |  | ON |  | Z2 dan Z3 | on | 0 |  | Z1 | Z2 | on | 0,05 | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000-05-01 |  | CT: 3,75; *OCR: 0,38; tms: 0,63; *GFR: 0,64 | [20 empty] | DKSI/10/04/2021/86
PHT.119 | CENGKARENG | TANGERANG | https://docs.google.com/spreadsheets/d/18jqihAmmeb2YC5TZsLMIy1aWMYLf-AeSuu5MZ9oHZ_Q/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000-05-01 | 150kV/100V |  | 0,016 | 0,016 | 0,06 | 1,29/0,67 | 9,23 | 82 |  | on | 1 | 0 | on | 10 | on |  | on | 10s |  | - |  | - |  | 82 |  | 0,949 | 5,502 | 5,502 | 0 |  | 1,424 | 10,881 | 10,881 | 0,4 |  | 2,041 | 10,994 | 10,994 | 1,6 |  | 0,96 |  |  | 0 |  | 1,44 | [5 empty] | Setting Terpasang |  |  |  | 2,063 |  |  | on |  | Z2 dan Z3 | on | 0 |  | Z1 | Z2 | ON | 0,05 | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000-05-01 |  | CT: 3,75; *OCR: 0,38; tms: 0,63; *GFR: 0,64 | [20 empty] | DKSI/10/04/2021/86
PHT.120 | CENGKARENG BARU | BANDARA SOEKARNO HATTA | https://docs.google.com/spreadsheets/d/1EkKq7YMaHRlfUW5Swjcx_w5QxNJkVmtLd-tOb3UCuwk/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 1000/1 A |  | CT: 0,89; *OCR: 0,43; tms: 0,15; *GFR: 0,69 | [20 empty] | TJBB/01/04/2019/52
PHT.121 | CENGKARENG BARU | BANDARA SOEKARNO HATTA | https://docs.google.com/spreadsheets/d/1OvlR6HmEdqGju8L5nGM4xZtiFr_YodYcBzsyiLyxnuw/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 1000/1 A |  | CT: 0,89; *OCR: 0,43; tms: 0,15; *GFR: 0,69 | [20 empty] | TJBB/01/04/2019/52
PHT.122 | CENGKARENG BARU | CENGKARENG | https://docs.google.com/spreadsheets/d/1HXicHZIQ-GaHmPJoF8vtEUceUxVAoEQiqCSAlFHGUrA/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 4000/1 A | 150kV/100V | 0,4 km | 0,12 | 89 | 0.69 | -12 deg |  | 0,2 A | 2 A | 30 | 150 | 0 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - |  |  | Measured + MCB | Standrad | Blocking |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 | 11,5 | Enabled | V< | Enabled | 15 | 6 | 165 | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 4000/1 A |  | 0,95 | 0,21 | - | - |  | 0,16 | 0,46 | - | - | - | -
PHT.123 | CENGKARENG BARU | CENGKARENG | https://docs.google.com/spreadsheets/d/1yfy5JZXISpMVw-R3sugttS_dRI-Hx6azWvD1B-sZDCI/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 4000/1 A | 150/100 | 0.4 | 0,12 | 89 | 0,69 | -12 |  | 0,2 | 2 | 30 | 150 | 0 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | Measured + MCB | Standrad | Blocking |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 | 11,5 | Enablked | V< | - | 15 | 6 | 165 | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | 4000/1 A |  | 0,95 | 235 | - | - |  | 0,16 | 485 | - | - | - | -
PHT.124 | CENGKARENG BARU | ITS | https://docs.google.com/spreadsheets/d/1TON7JqybXDQqv5vep4Ymt07iau7ilPQK1o_I-t6yI8o/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 767011 | 150/100 | 4,13 km | 6,88 | 87 | 0,67 | -4 |  | 0,2 | 2 | 30 | 150 | 0 | Disbaled | Disbaled | DIsbaled | DIsbaled | DIsbaled | DIsbaled | [6 empty] | 0 | 0,4 | 1,6 | PUR | - | Disabled | - | Enabled Poledead | 000011 | Enabled | 000011 | - |  | Measured+MCB | Standard | Disabled |  | 5,51 | 87 | - | 8,26 | 87 | - | 13,82 | 87 | - |  | 1PAR/3PAR | - | 1,5 | 1 | 3 |  | 52 | 11,5 | Enabled | V< | Enabled | 15 | 6 | 165 | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | CT: 4000/1 A; I>: 0,72; tms: 0,27; I>: 0,12; tms: 0,52
PHT.125 | CENGKARENG BARU | TANGERANG BARU | https://docs.google.com/spreadsheets/d/187-jnRs8IP1RBfMsN8Deaa19nu7R9MTbl6LW4Way4Lk/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 4000/1 A | 150/100 | 6,5 | 11 | 87 | 0.67 | -4 |  | 0,2 | 2 | 30 | 150 | 0 | Disbaled | Disbaled | DIsbaled | DIsbaled | DIsbaled | DIsbaled | [6 empty] | 0 | 0,4 | 1,6 | PUR | - | Disabled | - | Enabled poldead | 000011 | Enabled | 000011 | - |  | Measure + MCB | Standrad | Disabled |  | 8,8 | 87 | - | 19,08 | 87 | - | 32,48 | 87 |  |  | 1PAR/3PAR |  | 1,5 s | 1 | 3 |  | 52 | 11,5 | Enabled | V< | - | 15 | 6 | 165 | [11 empty] | OCR/GFR | Micom P643 |  | Setting Terpasang | CT: 4000/1 A; I>: 0,95; tms: 0,21; I>: 0,16; tms: 0,46 | [19 empty] | TJBB/01/04/2017/
PHT.126 | CILEDUG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/1qN3MTSsZnLG3qoJeJFPXVcBHA3Dub-C1AzliJvcwRiw/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 401769 | 150kV / 100V | 3,25km | 0,42 | 77 | 1,02 | -37 |  | 0,3 A | 2 A | 30% | 150% | 0 | [12 empty] | 0 | 0,4 | 1,6 | Disabled | -% | Disabled | -% | Enabled PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | Aktif |  | Measured + MCB | I DIff+ Std | - |  | 0,33 | 77 | 38,81 | 1,120 | 77 | 48,52 | 1,97 | 77 | 60,65 |  | Not Active |  |  |  |  | Disabled | [19 empty] | OCR/GFR | Schneider - Micom P142 |  | Setting Terpasang | CT: 401769; I>: 0,57; tms: 0,415; I>: 0,1; tms: 0,715 | [19 empty] | DKSI/19/03/2020/59
PHT.127 | CILEDUG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/1y_xOr_sxzk3LIPrpPEqdRzcuSHy-FasJkN1wOD-g8M0/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150kV/100 | 3,7 | 0,44 | 81 | 0,24 | 56 |  | 0,3 | 2 | 30% | 150% | 0 | DIsabled | DIsabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0,4 | 1,6 | PUR | -% | Disabled | -% | Enabled PoleDeada | 000110 (Z2 Z3) | Enabled | 110 |  |  | Measured + MCB | IDIff + STD |  |  | 0,35 | 81 | 25 | 0,88 | 81 | 27 | 1,2 | 81 | 31 |  | Not Active |  |  |  |  | Enabled | 52 V | 12 V |  | V< | Enabled | 15 | 6 | 125 mHz | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | CT: 2000/1; I>: 0,86; tms: 0,415; I>: 0,15; tms: 0,71 | - | - | [17 empty] | DKSI/19/03/2020/77
PHT.128 | CILEDUG | METLAND | https://docs.google.com/spreadsheets/d/1ju8zrULuJkIKPGtaIk07pjwv4dk_2KLfGRBcCPJn5H0/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 3200/1A | 150kV/100V | 5,360 km | 6,91 | 77 | 0,66 | 6 |  | 0,3 | 2 | 30 | 150 | 0 | Disabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0s | 0,4s | 1,6s | POR | 100ms | Disabled | - | Enabled Pole Dead | 000011(Z1 Z2) | Enabled | 000011(Z1 Z2) | SEF Enabled |  | Measured + MCB | I Diff + Std |  |  | 5,519 ohm | 77 | 42,9 | 8,291 ohm | 77 | 53,63 | 11,77 ohm | 77 | 67,03 |  | Not Active | [5 empty] | 52 v | 11,5 |  | V< | Enabled | 15 | 6 | 165 | [11 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | [30 empty] | TJBB/01/04/2022/010
PHT.129 | CILEDUG | METLAND | https://docs.google.com/spreadsheets/d/1iSOMAut5iinyns6FiHrDFv6I9zmGMSbvnura3yLC7Aw/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV/100V | 5,356 km | 4,32 | 77 | 0,66 | 6 |  | 0,3 | 2 | 30% | 150% | 0 | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0,4 | 1,6 | PUR | - | Disabled | - | Enabled Pole Dead | 000110 | Enabled | 000110 | - |  | Measured + MCB | I Diff + Std | Blocking |  | 3,449 ohm | 77 | 26,81 | 5,18 ohm | 77 | 33,52 | 7,36 ohm | 77 | 41,89 |  | Not Active | [5 empty] | 52 | 11,5 | - | V< | Enabled | 15 | 6 | 165mHz | [11 empty] | OCR/GFR | Alstom - Micom P14D |  | Setting Terpasang | CT: 2000-01-01; I>: 0,83; tms: 0,42; I>: 0,14; tms: 0,72 | - | - | [17 empty] | TJBB/01/04/2022/011
PHT.130 | DURIKOSAMBI | CENGKARENG | https://docs.google.com/spreadsheets/d/12gem_gMMrXhnbHhl0jNwMG1RQDewmRvv9KzYA2Gwz7o/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 2000-05-01 | 150/100 | 10,32 | 1.272 | 84 | 0,67 | -4 | 1% | 1 | 10 | 30 | 150 | 0 | - | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0,4 | 1,6 | POR | 0,1 | Disabled | - | Enabled Poledead | 0000000011 | Enabled | 0000000011 | - |  | Measure+MCB | Idiff+Std | Disbaled |  | 1,018 ohm | 84 | 5,81 | 1,528 ohm | 84 | 6,45 | 2,966 ohm | 84 | 7,17 |  | 1PAR/3PAR | Bar 3 Phase | 0,1 | 1 | 3 |  | 52 | 11,5 | Enabled | V< | Enabled | 15 | 6 | 0,165 | [11 empty] | OCR/GFR | SCHNEIDER - Micom P142 |  | Setting Terpasang | 2000 A / 5 A |  | 4,75 A | 0,45 | DISABLED | DISABLED |  | 0,75 A | 0,8 | DISABLED | DISABLED | DISABLED | DISABLED
PHT.131 | DURIKOSAMBI | CENGKARENG | https://docs.google.com/spreadsheets/d/1XHeabcATmoiXzbczrISnDosADc7FLjSsKrEqPhYAPXI/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Setting Terpasang | 2000-05-01 | 150/100 | 10,32 | 1.272 | 84 | 0,67 | -4 | 1% | 1 | 10 | 30 | 150 | 0 | - | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 | 0,4 | 1,6 | POR | 0,1 | Disabled | - | Enabled Poledead | 0000000011 | Enabled | 0000000011 | - |  | Measure+MCB | Idiff+Std | Disbaled |  | 1,018 ohm | 84 | 5,81 | 1,528 ohm | 84 | 6,45 | 2,966 ohm | 84 | 7,17 |  | 1PAR/3PAR | Bar 3 Phase | 0,1 | 1 | 3 |  | 52 | 11,5 | Enabled | V< | Enabled | 15 | 6 | 0,165 | [11 empty] | OCR/GFR | SCHNEIDER - Micom P142 |  | Setting Terpasang | 2000 A / 5 A |  | 4,75 A | 0,45 | DISABLED | DISABLED |  | 0,75 A | 0,8 | DISABLED | DISABLED | DISABLED | DISABLED
PHT.132 | DURIKOSAMBI | LMK | https://docs.google.com/spreadsheets/d/1OY291k7zDt6-eBiPIDrU8ww1TUMC9eLceEZx5LmCJY8/edit?usp=drive_link | MICOM P443 | Setting Terpasang |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | -328596 | 150 kV / 100 V |  | 0,3 km | 0,02 ohm | 80,54 deg | 0.699 | -1,848 deg | 0,01 ohm | 5,19 ohm | 5,19 ohm | 0 s | 1,41 ohm | 5,77 ohm | 5,77 ohm | 0,8 s | 2,25 ohm | 6,41 ohm | 6,41 ohm | 1.2 s | [6 empty] | POR | 0 s |  |  | Enabled PoleDead | 40 s | Disabled | [5 empty] | Measured + MCB | Disabled |  | Not Active | [34 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | -328596 |  | 4,68 A | 0,446 SI | Disabled | - |  | 0,78 A | 0,774 SI | Disabled | - | Disabled | Disabled
PHT.133 | DURIKOSAMBI | GROGOL BARU | https://docs.google.com/spreadsheets/d/1QzJPlrFj79drqDLs5dDCiJUchmUilWCCDucJv-SEK7c/edit?usp=drive_link | 7SL87 | Setting Terpasang | 1600A/5A | 150kV/100V |  | 0,016 | 0,016 | 0,06 | 1,29/0,67 | 6,47 | 82 |  | on | 1,25 | 0 | on | 12,5 | on |  | on | 10 |  | off |  | off |  | 82 |  | 0,310 | 4,68 | 4,68 | 0 |  | 0,465 | 5,2 | 5,2 | 0,4 |  | 0,609 | 5,77 | 5,77 | 1,6 |  | 0,313 |  |  |  |  | 0,469 | [5 empty] | Setting Terpasang |  |  |  | 614 |  |  | OFF |  | - | OFF | 0 |  | 21 z2 | 21 z2 | ON | 0,05 | [27 empty] | OCR/GFR | SCHNEIDER - P142 |  | Setting Terpasang | 1600 / 5 |  | 6 A | 0,4 | - | - |  | 1 A | 0,55 | - | - | - | -
PHT.134 | DURIKOSAMBI | GROGOL BARU | https://docs.google.com/spreadsheets/d/19Tta_Pgf8VceaAZbcgvL0zsjdPRefgPXwJDHrSeTZmw/edit?usp=drive_link | 7SL87 | Setting Terpasang | -109450 | 150kV/100V |  | 0,016 | 0,016 | 0,06 | 1,29/0,67 | 6,47 | 82 |  | on | 1,25 | 0 | on | 12,5 | 1,5 | 0 | on | 10 |  | off |  | off |  | 82 |  | 0,31 | 4,68 | 4,68 | 0 |  | 0,465 | 5,2 | 5,2 | 0,4 |  | 0,669 | 5,77 | 5,77 | 1,6 |  | 0,313 |  |  | 0 |  | 0,469 | [5 empty] | Setting Terpasang |  |  |  | 614 |  |  | off |  | off |  |  |  | 21 Z2 | 21 Z2 | on | 0,05 | [27 empty] | OCR/GFR | SCHNEIDER - P142 |  | Setting Terpasang | 1600 / 5 |  | 6 A | 0,4 | - | - |  | 1 A | 0,55 | - | - | - | -
PHT.135 | DURIKOSAMBI | KEBON JERUK | https://docs.google.com/spreadsheets/d/139OjcSqWTXj4CMRzKc1diiAOWKn-VyltKPQWtqG5c5E/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | ENABLED | ENABLED | DISABLED |  | Setting Terpasang | 1000 A / 5 A | 150 kV / 100 V | 10,2 km | 0,624 Ohm | 72 deg | 0,77 | -17 deg |  | 1,5 A | 10 A | 30 % | 150 % | 0 | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | [19 empty] | MCB Only | IDiff + Std | Blocking | [17 empty] | 52 V | 11,5 V | ENABLED | V < | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | SCHNEIDER - Micom P122 |  | Setting Terpasang | 4000 A / 5 A |  | 0,25 x In | 0,3 | No | No |  | 0,08 x Ien | 0,3 | No | No | No | No
PHT.136 | DURIKOSAMBI | KEBON JERUK | https://docs.google.com/spreadsheets/d/1oAq-UZ6qwvZAzGsVZiPZV6ZKqYY8WWNk875yfpl75LM/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | ENABLED | ENABLED | DISABLED |  | Setting Terpasang | 2000/5 A | 150 kV / 100 V | 10,2 km | 0,31 ohm | 73,74 deg | 0.773 | -17,448 deg |  | 1,5 A | 10 A | 30 % | 150 % | 0 | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | [19 empty] | MCB Only | IDiff + Std | Blocking |  | 0,25 ohm | 73,74 deg | 8,80 ohm | 0,42 ohm | 73,74 deg | 9,78 ohm | 0,71 ohm | 73,74 deg | 10,87 ohm | [7 empty] | 52 V | 11,5 V | ENABLED | V < | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | SCHNEIDER - Micom P122 |  | Setting Terpasang | 2000-05-01 |  | 2,76 | 0,421 SI | - | - |  | 0,46 | 0,748 SI | - | - | - | -
PHT.137 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/1oe8ujMX_JkOGE_FO4BV0bOCyLh1uOKWT9sSxtYehSV4/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | ENABLED | ENABLED | DISABLED |  | Setting Terpasang | -328596 | 150/100 | 6.84 | 0.574 | 73 | 0.77 | -17 | ENABLED | 1 | 10 | 30 | 150 | 0 | - | - | - | - | - | - | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | MEASURE+MCB | IDIFF+STD | NA |  | - | - | - | - | - | - | - | - | - |  | Not Active | [5 empty] | 52 | 11.5 | NA | V< | ENABLED | 15 | 6 | 0.1 | [11 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | -328596 | ENABLED | 4.75 | 0.525 | - | - | ENABLED | 0.75 | 0.85 | - | - | - | -
PHT.138 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/1OrmBeE4PMXy4O0pfhkM3858KR7KEvptf74AklLTRUKU/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | ENABLED | ENABLED | DISABLED |  | Setting Terpasang | -328596 | 150/100 | 6.84 | 0.574 | 73 | 0.77 | -17 | ENABLED | 1 | 10 | 30 | 150 | 0 | - | - | - | - | - | - | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | MEASURE+MCB | IDIFF+STD | NA |  | - | - | - | - | - | - | - | - | - |  | Not Active | [5 empty] | 52 | 11.5 | NA | V< | ENABLED | 15 | 6 | 0.1 | [11 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | -328596 | ENABLED | 4.75 | 0.525 | - | - | ENABLED | 0.75 | 0.85 | - | - | - | -
PHT.139 | DURIKOSAMBI | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1p3nXTV53M5HPzYrRfyiqmUNPrTQsI37swmSfllTyM5Y/edit?usp=drive_link | RED670 | Setting Terpasang | 4000 / 5 A | 150 kV / 100 V |  | 0.2 ib | - | -% | -% | - | 1 | 0 | - | - | - | - | -% |  | 80 | - | - | - | - | 30 | - | - | On | 0 s | 2,07 | 0,32 | 2,07 | 0,32 | 6,22 | 0,57 | 4,35 | 15,62 | 0 s | On | 5,71 | 0,87 | 17,12 | 1,56 | [5 empty] | Setting Terpasang | 11,98 | 22,32 | 0.4 s | On | 9,92 | 1,51% | 29,76 | 2,72 | 20,84 | 31,88 | 1.6 s |  | On | DLD Disable |  | On |  | 0,165 ohm | 2,374 ohm | 0,225 ohm | 2,772 ohm | 0,395 ohm | 2,591 ohm | 0,71 ohm | 7,774 ohm | 2,1 km |  | PUR | -% |  |  | Off | [5 empty] | On |  | 1 | 3 |  | On |  |  |  |  | Setting Terpasang | 0,10pu | 0,167 | 15 | [6 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 4000 / 5 A |  | 3.8 A | 0.385 SI | - | - |  | 0.65 A | 0.775 SI | - | -
PHT.140 | DURIKOSAMBI | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1AQJHBJ3OULojzO979M0lmk6fExy2VRM0dQY2KNNRlrk/edit?usp=drive_link | RED670 | Setting Terpasang | 4000 / 5 A | 150 kV / 100 V |  | 0.2 ib | - | -% | -% | - | 1 | 0 | - | - | - | - | -% |  | 80 | - | - | - | - | 30 | - | - | On | 0 s | 2,07 | 0,32 | 2,07 | 0,32 | 6,22 | 0,57 | 4,35 | 15,62 | 0 s | On | 5,71 | 0,87 | 17,12 | 1,56 | [5 empty] | Setting Terpasang | 11,98 | 22,32 | 0.4 s | On | 9,92 | 1,51% | 29,76 | 2,72 | 20,84 | 31,88 | 1.6 s |  | On | DLD Disable |  | On |  | 0,165 ohm | 2,374 ohm | 0,225 ohm | 2,772 ohm | 0,395 ohm | 2,591 ohm | 0,71 ohm | 7,774 ohm | 2,1 km |  | PUR | -% |  |  | Off | [5 empty] | On |  | 100% | 300% |  | On |  |  |  |  | Setting Terpasang | [9 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 4000 / 5 A |  | 3.8 A | 0.35 SI | - | - |  | 0.75 A | 0.675 SI | - | -
PHT.141 | TANGERANG | CENGKARENG | https://docs.google.com/spreadsheets/d/1WDQtAVRWVcMBXEYNrTaze76UdxxwbbtRifsBtPVoLfE/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000/5 A | 150kV/100V |  | 0,016 | 0,016 | 0,06 | 1,29/0,67 | 9,23 | 82 |  | on | 1 | 0 | On | 10A | on |  | on | 10s |  |  |  | on |  | 82 |  | 0,949 | 5,5 | 5,555 | 0 |  | 1,424 | 10,834 | 10,889 | 0,8 |  | 2,943 | 11,057 | 11,139 | 1,6 |  | 0,96 |  |  |  | 0 | 1,44 | [5 empty] | Setting Terpasang |  |  |  | 2996 |  |  |  |  | 21 Z2, 21 Z3 | on | 0 |  | z1 | z2 | on | 0,05 | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000-05-01 |  | CT: 3,75; *OCR: 385; tms: 0,63; *GFR: 0,64 | [20 empty] | DKSI/10/40/2021/87
PHT.142 | TANGERANG | CENGKARENG | https://docs.google.com/spreadsheets/d/1doRtkPD9VDq8BogaGbLM6VHPATJ25QnPRsghj_ox_Jc/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000/5 | 150kV/100V |  | 0,016 | 0,016 | 0,06 | 1,29/0,667 | 9,23 | 82 |  | on | 1 | 0 | on | 10 | on |  | on | 10s |  |  |  | off |  |  |  | 0,949 | 5,5 | 5,555 | 0s |  | 1,424 | 10,834 | 10,889 | 0,8s |  | 2,493 | 11,057 | 11,139 | 1,6 |  | 0,96 |  |  | 0 |  | 1,44 | [5 empty] | Setting Terpasang |  |  |  | 2,996 |  |  | on |  | 21 Z2 | on | 0 |  | 21 Z1 | 21 Z2 | on | 0 | [27 empty] | OCR/GFR | Siemens - 7SJ82 |  | Setting Terpasang | 2000-05-01 |  | CT: 3,75; *OCR: 0,38; tms: 0,63; *GFR: 0,64 | [20 empty] | DKSI/10/40/2021/87
PHT.143 | TANGERANG | JATAKE BARU | https://docs.google.com/spreadsheets/d/1kLS7j2k8e3kLE9juhB96sMb6rlJJCvcUG1V-o0urseU/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150/100 | 2000-05-01 |  | 0,514 | 0,071 | 1,543 | 0,346 | 33,966 | 11,731 | 6,87 |  | 1 | 1 | 1 | 1 |  | 0,678 | -0,085 | 82 | 0,415 | 0 | 0,415 | 0 | 0,623 | 0,4 | 0,623 | 0,4 | 0,943 | 1,6 | 0,943 | 1,6 | 0,623 |  | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | Schneider - Micom P122 |  | Setting Terpasang | 2000-05-01 |  | 0,97xIn | 0,355 (SI) | - | - |  | 0,16 | 0,61 | - | - | - | - | [12 empty] | TJBB/01/04/2021/36
PHT.144 | TANGERANG | JATAKE BARU | https://docs.google.com/spreadsheets/d/1P5Pa3Gc7z8qCCGEBMA8aaHbBDhOp7gU8hFN4iD2QPTg/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150/100 | 2000-05-01 |  | 0,514 | 0,071 | 1,543 | 0,346 | 33,966 | 11,731 | 6,87 |  | 1 | 1 | 1 | 1 |  | 0,678 | -0,085 | 82 | 0,415 | 0 | 0,415 | 0 | 0,623 | 0,4 | 0,623 | 0,4 | 0,943 | 1,6 | 0,943 | 1,6 | 0,623 |  | POTT |  | Disable | Enable |  | Disable | Disable | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | Schneider - Micom P122 |  | Setting Terpasang | 2000-05-01 |  | 0,972 | 0,355 SI | - | - |  | 0,162 A | 0,61 | - | - | - | - | [12 empty] | TJBB/01/04/2021/36
PHT.145 | ALAM SUTERA | CILEDUG | https://docs.google.com/spreadsheets/d/1JchLGM_8JGuJ2UJzWXbOd_34ffbV58XmDC4FQaoDEjw/edit?usp=drive_link | MICOM P543 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 4000 / 1 A | 150 kV / 100 V | 3,25 km | 0,56 ohm | 77 deg | 1,02 | -37 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | Disabled | - | Disabled | - | Enabled PoleDead | 000110 | Enabled | 000110 | - |  | Measured + MCB | Standard | - |  | 0,44 ohm | 77 deg | 51,75 ohm | 1,510 ohm | 77 deg | 64,69 ohm | 2,660 ohm | 77 deg | 80,86 ohm |  | Not Active | [24 empty] | OCR/GFR | Alstom - Micom P141 |  | Setting Terpasang | 2000/1 A | Group 1 | 0,86 A | 0,415 (SI) | - | - | Group 1 | 0,14 A | 0,705 (SI) | - | - | - | - | [17 empty] | DKSI/25/03/2022/026
PHT.146 | ALAM SUTERA | CILEDUG | https://docs.google.com/spreadsheets/d/1mN0pVb9fDYDO035ti54lDmQmiSVbFuze2mvEuH3uui4/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Setting Terpasang | 2000 / 1 A | 150 kV / 100 V | 3,7 km | 0,44 ohm | 81 deg | 0,24 | 56 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0,4 s | 1,2 s | PUR | 0 s | Disabled | - | Enabled PoleDead | 000110 | Enabled | 000110 | - |  | Measured + MCB | IDiff + Std | - |  | 0,35 ohm | 81 deg | 25 ohm | 0,89 ohm | 81 deg | 27 ohm | 1,53 ohm | 81 deg | 31 ohm |  | Not Active | [24 empty] | OCR/GFR | Alstom - Micom P141 |  | Setting Terpasang | 2000/1 A | Group 1 | 0,86 A | 0,415 (SI) | - | - | Group 1 | 0,15 A | 0,7 (SI) | - | - | - | - | [17 empty] | DKSI/23/03/2021/57
PHT.147 | ALAM SUTERA | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/1gAeuD7_hhenIiw6X-N4CzMGpDDdgqFXuWll6Xg-r-fU/edit?usp=drive_link | RED670 | Setting Terpasang | 2000/1 A | 150kV/100V |  | 0.2 Ibase | 1,25 | 2 | 30% | 80% | [17 empty] | 0s | 0,88 | 0,13 | 0,88 | 0,13 | 2,62 | 0,94 | 1,84 | 24,55 | 0s |  | 1,36 | 0,2 | 4,08 | 1,46 | [5 empty] | Setting Terpasang | 2,85 | 35,07 | 0,4 |  | 3,22 | 0,33 | 9,67 | 2,65 | 6,77 | 50,1 | 1,6s |  | On | DLD Disabled |  |  |  | 0,259 | 3,427 | 0,266 | 3,415 | 0,157 | 1,093 | 1,177 | 3,28 | 7,2 |  | permOr |  |  |  | off |  |  | On | UzslZs |  | off |  |  |  |  | On |  |  |  |  | Setting Terpasang | [9 empty] | OCR/GFR | Alstom - Micom P141 |  | Setting Terpasang | 2000/1 A |  | 0.91 A | 0.4 SI | - | - |  | 0.15 A | 0.695 SI | - | -
PHT.148 | ALAM SUTERA | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/1lfft6hnMraU0pzLBcTbd3Ilop914Sdx_QEoqrEMglk8/edit?usp=drive_link | RED670 | Setting Terpasang | 2000/1 A | 150kV/100V |  | 0.2 Ibase | 1,25 | 2 | 30% | 80% | [17 empty] | 0s | 0,88 | 0,13 | 0,88 | 0,13 | 2,62 | 0,94 | 1,84 | 24,55 | 0s |  | 1,36 | 0,2 | 4,08 | 1,46 | [5 empty] | Setting Terpasang | 2,85 | 35,07 | 0,4 |  | 3,22 | 0,33 | 9,67 | 2,65 | 6,77 | 50,1 | 1,6s |  | On | DLD Disabled |  |  |  | 0,259 | 3,427 | 0,266 | 3,415 | 0,157 | 1,093 | 1,177 | 3,28 | 7,2 |  | permOr |  |  |  | off |  |  | On | UzslZs |  | off |  |  |  |  | On |  |  |  |  | Setting Terpasang | [9 empty] | OCR/GFR | Alstom - Micom P141 |  | Setting Terpasang | 2000/1 A |  | 0.91 A | 0.4 SI | - | - |  | 0.15 A | 0.695 SI | - | -
PHT.149 | KEMBANGAN | METLAND | https://docs.google.com/spreadsheets/d/19nEK6VrdppxmpRcAmCTt8rKTmgYKyWNNGtkXSIdXHSg/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 474938 | Group 1 | CT: 2,6 A; *OCR: 0,43; I>>: Group 1; tms: 0,45 A; *GFR: 0,75
PHT.150 | KEMBANGAN | METLAND | https://docs.google.com/spreadsheets/d/1NANLIITCPB2AS9A4bNKUEYQCK53VaAY8s-AKxthNW2A/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR | SCHNEIDER - MICOM P142 |  | Setting Terpasang | 474938 | Group 1 | CT: 2,6 A; *OCR: 0,425; I>>: Group 1; tms: 0,45 A; *GFR: 0,75
PHT.151 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/167url0Bt7IuvsrwV3Wlt9uVQ-XMxTkI90p4S6ymZSlo/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | ENABLED | ENABLED | DISABLED |  | Setting Terpasang | -328596 | 150/100 | 6.84 | 0.574 | 73 | 0.77 | -17 | ENABLED | 1 | 10 | 30 | 150 | 0 | - | - | - | - | - | - | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | MEASURE+MCB | IDIFF+STD | NA |  | - | - | - | - | - | - | - | - | - |  | Not Active | [5 empty] | 52 | 11.5 | NA | V< | ENABLED | 15 | 6 | 0.1 | [11 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | -328596 |  | 4.75 | 0.475 | DISABLED | - |  | 0.75 | 0.8 | DISABLED | - | - | - | [17 empty] | DKSI/22/01/2020/64
PHT.152 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/10N9GvgG9WxD1cMlm7VmLlzCOnnOdRyQ-HerOmnYTI_s/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | ENABLED | DISABLED | DISABLED | DISABLED | ENABLED | ENABLED | DISABLED |  | Setting Terpasang | -328596 | 150/100 | 6.84 | 0.574 | 73 | 0.77 | -17 | ENABLED | 1 | 10 | 30 | 150 | 0 | - | - | - | - | - | - | [6 empty] | - | - | - | -% | -% | -% | - | - | - | - | - | - |  | MEASURE+MCB | IDIFF+STD | NA |  | - | - | - | - | - | - | - | - | - |  | Not Active | [5 empty] | 52 | 11.5 | NA | V< | ENABLED | 15 | 6 | 0.1 | [11 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | -328596 |  | 4.75 | 0.475 | DISABLED | - |  | 0.75 | 0.8 | DISABLED | - | - | - | [17 empty] | DKSI/22/01/2020/64
PHT.153 | KEMBANGAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1WKkODzeTLuKPPCL6z-OrPXqu14ChOAqt0CYzkiR76pM/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | N/A | N/A | Enabled | Disabled | Disabled | N/A | Disabled | N/A | Disabled | Disabled | N/A | N/A | N/A | Disabled | Disabled | Disabled | N/A |  | Setting Terpasang | 1000 / 5 A | - | - | - | - | - | - |  | 0.2 In | 2 In | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - | - | - | - | - | - |  |  | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | AREVA - MICOM P123 |  | Setting Terpasang | -328596 |  | 5.55 | 0.5 | - | - |  | 0.925 | 0.825 | - | - | - | -
PHT.154 | KEMBANGAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1KpBWwyrMVRSi2zJV0aTTMb7s8_MI9zGmDUd10HaFGcs/edit?usp=drive_link | MICOM P546 | Setting Terpasang |  | Enabled | N/A | N/A | Enabled | Disabled | Disabled | N/A | Disabled | N/A | Disabled | Disabled | N/A | N/A | N/A | Disabled | Disabled | Disabled | N/A |  | Setting Terpasang | 1000 / 5 A | - | - | - | - | - | - |  | 0.2 In | 2 In | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - | - | - | - | - | - |  |  | - | - | - | - |  | - | - | - | - | - | - | - | - | [11 empty] | OCR/GFR | AREVA - MICOM P123 |  | Setting Terpasang | -328596 |  | 5.55 | 0.5 | - | - |  | 0.925 | 0.825 | - | - | - | -
PHT.155 | KEMBANGAN | PETUKANGAN | https://docs.google.com/spreadsheets/d/1t31_j4b_xKzqeXfrqTvB4JKvS1t73HS8y7kAAWPio5w/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/5A |  | 0.585 ohm | 0.093 ohm | 1.412 ohm | 0.395 ohm | 0 ohm | 0 ohm | 9.52 km |  | 1 A | 1 | Enabled | Disabled |  | 0.486 | -0.095 | 80.966 deg | 0.474 ohm | 0 s | 0.474 ohm | 0 s | 0.711 ohm | 0.4 s | 0.711 ohm | 0.4 s | 1.384 ohm | 1.6 s | 1.384 ohm | 1.6 s | 0.711 ohm | Z1, Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | 2000-05-01 | ENABLED | 6 | 0.44 | DISABLED | - | ENABLED | 1 | 0.77 | DIABLED | - | DISABLED | DISABLED
PHT.156 | KEMBANGAN | PETUKANGAN | https://docs.google.com/spreadsheets/d/1zmIRITbtSDzGzlGqLszJtZFF3WSEBbEZ-yVWIca5FcI/edit?usp=drive_link | PCS-931 | Setting Terpasang | 150kV/100V | 2000/5A |  | 0.585 ohm | 0.093 ohm | 1.412 ohm | 0.395 ohm | 0 ohm | 0 ohm | 9.52 km |  | 1 A | 1 | Enabled | Disabled |  | 0.486 | -0.095 | 80.966 deg | 0.474 ohm | 0 s | 0.474 ohm | 0 s | 0.711 ohm | 0.4 s | 0.711 ohm | 0.4 s | 1.384 ohm | 1.6 s | 1.384 ohm | 1.6 s | 0.711 ohm | Z1, Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [10 empty] | OCR/GFR | Alstom - Micom P142 |  | Setting Terpasang | 2000-05-01 | ENABLED | 6 | 0.44 | DISABLED | - | ENABLED | 1 | 0.77 | DIABLED | - | DISABLED | DISABLED
PHT.157 | METLAND | KEMBANGAN | https://docs.google.com/spreadsheets/d/179_CH1lkXiKt-J1FguRux5erjkhXOw1ivyXQjf9OZbg/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000-01-01 | 150kV/100V |  | 0.01 miuF/km | 0.01 miuF/km | 0.383 Ohm/km | 0.08/0.67 | 2.61 km | 23.66 deg |  | ON | 0.2 A | 0 s | ON | 2 A | no |  | ON | 10 s |  | ON |  | OFF |  | 83.8 |  | 0.799 Ohm | 28.577 Ohm | 1.867 Ohm | 0 s |  | 1.439 Ohm | 55.441 Ohm | 2.064 Ohm | 0.8 s |  | 2.953 Ohm | 56.696 Ohm | 3.319 Ohm | 1.6 s |  | On | 1.99 Ohm | 0 s | Yes | - | - | - |  | ON | 2.985 Ohm | 0.8 s | No | - | [5 empty] | Setting Terpasang | - | - |  | ON | 4.41 Ohm | 1.6 s | No | - | - | - |  |  | OCR/GFR/Z1/Z2 | ON | 0 s |  | Z1/Z2/Z1MHO/Z2MHO | Z2/Z2MHO | ON | 0.05 s | [16 empty] | OCR/GFR | 7SJ82 |  | Setting Terpasang | 2000-01-01 |  | 0,827 A | 0.43 | OFF | OFF |  | 0,138 A | 0.75 | OFF | OFF | OFF | OFF
PHT.158 | METLAND | KEMBANGAN | https://docs.google.com/spreadsheets/d/1Cjyd2jz0C-e2Dwbb_jPFq1_UZiZcvp5FintVJFAL4q8/edit?usp=drive_link | 7SL87 | Setting Terpasang | 2000-01-01 | 150KV/100V |  | 0.01 | 0.01 | 0.383 | 0.08/0.67 | 2.61 | 23.66 |  | ON | 0.2 A | 0 s | ON | 2 A | - |  | ON | 3 s |  | Z1 Z2 Z3 Z4 Z1MHO Z2MHO Z3MHO Z4MHO |  | OFF |  | 83.8 |  | 0.799 Ohm | 28.577 Ohm | 1.867 Ohm | 0 s |  | 1.439 Ohm | 55.441 Ohm | 2.064 Ohm | 0.8 s |  | 2.953 Ohm | 56.696 Ohm | 3.319 Ohm | 1.6 s |  | On | 1.99 Ohm | 0 s | Yes | - | - | - |  | ON | 2.985 Ohm | 0.8 s | No | - | [5 empty] | Setting Terpasang | - | - |  | ON | 4.41 Ohm | 1.6 s | No | - | - | - | - |  | OCR GFR Z1 Z2 | ON | 0 s |  | Z1 Z2 Z1MHO Z2MHO | Z2 Z2MHO | ON | 0.05 s | [16 empty] | OCR/GFR | 7SJ82 |  | Setting Terpasang | 2000-01-01 |  | 0.827 A | 0.43 | OFF | OFF |  | 0.138 A | 0.75 | OFF | OFF | - | -
PHT.159 | METLAND | CILEDUG | https://docs.google.com/spreadsheets/d/1VEww-qRd52g7ojdAmLqyodaxK6VH3YTHkO81Ssy7KFM/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Group 1 | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150KV/100KV | 5.360 KM | 4.320 Ohm | 77 deg | 0.66 | 6 deg |  | 0.3 mA | 2 A | 30 % | 150 % | 0 | DISABLE | DISABLE | DISABLE | DISABLE | DISABLE | DISABLE | [6 empty] | 0s | 0.8s | 1.6s | PUR |  | DISABLE |  | enable poledead | 000110 (Z2 Z3) | enable | 000110 (Z2 Z3) | BELUM |  | MEASURE + MCB | BLOCKING | ENABLE |  | 3.452 Ohm | 77.091 deg | 26.81 Ohm | 5.178 Ohm | 77.091 deg | 33.51 Ohm | 5.512 Ohm | 77.091 deg | 41.9 Ohm |  | Not Active | [5 empty] | 52 V | 11.5 V | ENABLE | V< | Enabled | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | SIEMENS 7SJ82 |  | Setting Terpasang | 2000-01-01 |  | 0,87 A | 0.43 | OFF | OFF |  | 0,138 A | 0.75 | OFF | OFF | OFF | OFF
PHT.160 | METLAND | CILEDUG | https://docs.google.com/spreadsheets/d/1bZ9XHIPIKVQQrKIzDS1Zvo5UXruEg1dK4wxT5CiejFs/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Group 1 | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000-01-01 | 150KV/100KV | 5.360 KM | 4.32 Ohm | 77 deg | 0.66 | 6 deg |  | 0.3 mA | 2 A | 30 % | 150 % | 0 s | DISABLE | DISABLE | DISABLE | DISABLE | DISABLE | DISABLE | [6 empty] | 0 s | 0.8 s | 1.6 s | PUR | - | DISABLE | - | ENABLE POLEDEAD | Z2 Z3 | ENABLE | Z2 Z3 | BELUM |  | MEASURE + MCB | BLOCKING | ENABLE |  | 3.452 Ohm | 77.091 deg | 26.81 Ohm | 5.178 Ohm | 77.091 deg | 33.51 Ohm | 5.512 Ohm | 77.091 deg | 41.9 Ohm |  | Not Active | - | - | - | - |  | 52 V | 11.5 V | ENABLE | V< | ENABLE | 15 deg | 6 V | 0.165 Hz | [11 empty] | OCR/GFR | SIEMENS 7SJ82 |  | Setting Terpasang | 2000-01-01 |  | 0.827 A | 0.43 | OFF | OFF |  | 0.138 A | 0.75 | OFF | OFF | OFF | OFF
PHT.161 | SUMMARECON GADING SERPONG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/114A2IquyW1w_Elx655JgkryY-P1CmKq6elV4me_qcfw/edit?usp=drive_link | RED670 | Setting Terpasang | 2000/1A | 150kV/100V |  | 0,2 Ibase | 1,25 | 2 | 30% | 80% | 0,8 | 0,800 | 15 | 30 | [13 empty] | 0 | 0,88 | 0,13 |  |  | 2,62 | 0,94 | 1,84 | 24,55 | 0 |  | 1,31 | 0,19 | 3,94 | 1,41 | [5 empty] | Setting Terpasang | 2,76 | 35,07 | 0,4 |  | 8,05 | 0,69% | 24,15% | 5,3 | 16,91 | 50,1 | 1,6 |  | On | DLD disabled |  | On |  | 266 | 3451 | 259 | 3472 | 157 | 1,093 | 1,177 | 3,26 | 7,2 |  | permOR | [9 empty] | off |  |  |  |  | off |  |  |  |  | Setting Terpasang | [9 empty] | OCR/GFR | ABB - REF615E |  | Setting Terpasang | 2000-01-01 |  | 0,91xIn | 0,4 | - | - |  | 0,15xIen | 0,69 | - | - | - | - | [8 empty] | UITJBB/0/04/2019/088
PHT.162 | SUMMARECON GADING SERPONG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/1KWa9-PZ8g1_KvdAUqxqErVkca4WdxXGNVzL2ebE0Cpo/edit?usp=drive_link | RED670 | Setting Terpasang | 2000-01-01 | 150kV/100V |  | 0,2 | 1,25 | 2 | 30% | 80% | 0,8 |  | 15% | 30% | off | [12 empty] | 0s | 0,875 ohm | 0,13 |  |  | 2,62 | 0,94 | 1,84 | 24,55 | 0 |  | 1,31 ohm | 0,19 | 3,94 | 1,41 | [5 empty] | Setting Terpasang | 2,76 | 35,07 | 0,4 |  | 8,05 ohm | 0,69 | 24,15 | 5,30 | 16,91 | 50,10 | 1,6 |  | on | DLD disabled |  | On |  | 266 | 3451 | 259 | 3472 | 157 | 1,093 | 1,177 | 3,26 | 7,2 |  | permOr | [6 empty] | On | UZslZs |  | off |  |  |  |  | off |  |  |  |  | Setting Terpasang | [9 empty] | OCR/GFR | ABB - REF615E |  | Setting Terpasang | 2000-01-01 |  | 0,91xIn | 0,4 | - | - |  | 0,15xIen | 0,69 | - | - | - | - | [8 empty] | UITJBB/0/04/2019/088
PHT.163 | SUMMARECON GADING SERPONG | CURUG | https://docs.google.com/spreadsheets/d/1b89Yr8Sb190GQEFnO6G5zemn5Ku4ehDsvs7xwiBoSMc/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV/100V | 4,7 km | 0,570 ohm | 81 deg | 860 | -31 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | 0 s | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 | - |  | Measured + MCB | IDiff + Std | Blocking |  | 0.45 ohm | 81 deg | 31,49 ohm | 1.88 ohm | 81 deg | 34,99 ohm | 6.25 ohm | 81 deg | 38,88 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | ABB - REF615E |  | Setting Terpasang | 2000/1 A | Group 1 | 0.87 A | 0.41 SI | - | - | Group 1 | 0.145 A | 0.7 SI | - | - | Disabled | Disabled | [17 empty] | UITJBB/01/04/2019/084
PHT.164 | SUMMARECON GADING SERPONG | CURUG | https://docs.google.com/spreadsheets/d/19Al_PWI0Qw-CKb9WkhT3jHx0EY8L_6bgvAY0Rt5HkAY/edit?usp=drive_link | MICOM P545 | Setting Terpasang |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Setting Terpasang | 2000/1 A | 150kV/100V | 4,7 km | 0,570 ohm | 81 deg | 860 | -31 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | 0 s | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 | - |  | Measured + MCB | IDiff + Std | Blocking |  | 0.45 ohm | 81 deg | 31,49 ohm | 1.89 ohm | 81 deg | 34,99 ohm | 6.25 ohm | 81 deg | 38,88 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0,165 Hz | [11 empty] | OCR/GFR | ABB - REF615E |  | Setting Terpasang | 2000/1 A | Group 1 | 0.87 A | 0.41 SI | - | - | Group 1 | 0.145 A | 0.7 SI | - | - | Disabled | Disabled | [17 empty] | UITJBB/01/04/2019/084
PHT.165 | DURIKOSAMBI | GANDUL | https://docs.google.com/spreadsheets/d/19botCaaavxDBaf-vARrZlUhyojcuz9Rbbh_3pnyAtjE/edit?usp=drive_link | GRL 200 | Setting Terpasang |  | 767011 | 500kV/100V |  | On | 34 | 7.64 | 0.67 | 22.44 | 4.66 |  |  | Mho | 10 Ohm | On | 23 Ohm | 37 deg | 23 Ohm | 6.14 Ohm | 0 | 85 deg | 9.21 Ohm | 0.8 s | 85 deg | 14.75 Ohm | 1.2 s | Quad | 10 Ohm | On | 25 Ohm | 37 deg | 6.19 Ohm | 85 deg | 21 Ohm | 0 | 9.17 Ohm | 85 deg | 23.3 Ohm | 0.8 s | 14.5 Ohm | [5 empty] | 85 deg | 25.9 Ohm | 1.2 s |  | PUP | 0.1 s |  | On | 0 s | 0.10 s | off | off | off | off | On | On | Off | - | - | - | - | - | - |  | On | 0.18 A | 1.8 A | 30% | 80% | 0 | 0 s | Off | Off | Non | Off | Non | 1P | [16 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.166 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/11BV33oYcBclStuVCuJZ7V96PSV7fhb_zHswq3X7Z2Io/edit?usp=drive_link | GRL 200 | Setting Terpasang |  | 767011 | 500kV/100V |  | On | 3.9 | 0.93 | 0.05 | 4.2 | 1.93 |  |  | Mho | 10 Ohm | On | 23 Ohm | 37 deg | 86 deg | 0.75 Ohm | 0 s | 86 deg | 5.10 Ohm | 0.4 s | 86 deg | 9.28 Ohm | 1.6 s | Quad | 10 ohm | On | 23 ohm | 37 deg | 0.74 ohm | 86 deg | 21 Ohm | 0 s | 5.08 | 86 deg | 23.3 Ohm | 0.4 s | 9.24 ohm | [5 empty] | 86 deg | 23.3 Ohm | 1.6 s |  | PUP | 0.1 s |  | Off |  |  |  | Off |  |  |  |  | Off | [7 empty] | On | 0.22 A | 3 A | 30% | 80% |  | 0 s | Off | Off | Non | On | Non | 1P | [16 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.167 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/14AlF79AraBJTeGh9qkIwk3s73H_7xgfBZyKW8Pwv9ns/edit?usp=drive_link | RED670 | Setting Terpasang | [45 empty] | Setting Terpasang | [47 empty] | Setting Terpasang | [8 empty] | *OCR: OCR/GFR; I>>: Setting Terpasang
PHT.168 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/1dzxuS-kaeIJKCwYQctaWZz4BLbJCilVkltEeraPu1d0/edit?usp=drive_link | RED670 | Setting Terpasang | [45 empty] | Setting Terpasang | [47 empty] | Setting Terpasang | [8 empty] | *OCR: OCR/GFR; I>>: Setting Terpasang
PHT.169 | DURIKOSAMBI | GANDUL | https://docs.google.com/spreadsheets/d/1qoEK7SsH6Gy9AeMYtLG1S3L3Tnqz4qTUu2Axm6lwaoE/edit?usp=drive_link | PCS-931 | Setting Terpasang | 500kV/100V | 767011 |  | 7.649 | 0.678 | 22.445 | 4.66 | - | - | 34.093 |  |  | 1 | 1 | 0,04% |  | 0.68 | -0.12 | 85 | 6.143 | 0 | 6.143 | 0 | 9.215 | 0.8 | 9.215 | 0.8 | 14.75 | 1.2 | 14.75 | 1.2 | 9.215 | Z2 and Z3 | PUTT | [7 empty] | Enable | [14 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.170 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/1d_AKQc0gJyCAP-iRNKw2R-DeEPn-Yz7-7oaCY3nEewA/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.171 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/16rxOCvaN_bd9qM1Pwedxa2TICeufOdtdjf2Vsd9RMcg/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.172 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/1l3DP_rtaIzlRxs49FWFlXOqB3M1q9iRdnGOS8iYSPRA/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.173 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1E1ypR8s3N8wv1w3IrqS3cErlpvXo_TK3H_PDwmd-Dhk/edit?usp=drive_link | GRL 200 | Setting Terpasang | [98 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.174 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/19fOcmB5XJClL6YUBYhyUzFlL8Q2bYuiKm-mpqiXpKmI/edit?usp=drive_link | GRL 200 | Setting Terpasang | [98 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.175 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/14lQs5k6qf3O2swxH6HfjlTvqF_WgmJSAdpS-rJdRj_U/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.176 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/1Vw3_-zf-Ka1O5vV0kmLORYNd18vCxnySllxGtUJVQIU/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.177 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1WjPj7DDPLm96jjJtSsM-UfYyQXnLVY6ifcBsJvG4F5Q/edit?usp=drive_link | GRL 200 | Setting Terpasang |  | 2000-01-01 | 500kV/100V |  | On | 30.1 km | 8.46 Ohm | 0.75 Ohm | 25.39 Ohm | 5.72 Ohm |  |  | Mho | 2.5 Ohm | On | 19 Ohm | 10 deg | 84 deg | 2.72 Ohm | 0 s | 84 deg | 4.07 Ohm | 0.4 s | 84 deg | 13.27 Ohm | 1.6 s | Quad | 10 Ohm | On | 40 Ohm | 10 deg | 2.7 Ohm | 84 deg | 4.27 Ohm | 0 s | 4.06 s | 84 deg | 8.32 Ohm | 0.4 s | 12.94 Ohm | [5 empty] | 84 deg | 10.99 ohm | 1.6 s |  | PUP | 0.1 s |  | POP | 0.15 s | 0.1 s | Off | Off | Off | Off | On | On | Off | Off | M2 | Off |  |  |  |  | On | 0.73 A | 3.6 A | 30% | 80% | On | 0 s | Off | Off | Non | On | Block | 1P | [16 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.178 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1WjPj7DDPLm96jjJtSsM-UfYyQXnLVY6ifcBsJvG4F5Q/edit?usp=drive_link | GRL 200 | Setting Terpasang |  | 2000-01-01 | 500kV/100V |  | On | 30.1 km | 8.46 Ohm | 0.75 Ohm | 25.39 Ohm | 5.72 Ohm |  |  | Mho | 2.5 Ohm | On | 19 Ohm | 10 deg | 84 deg | 2.72 Ohm | 0 s | 84 deg | 4.07 Ohm | 0.4 s | 84 deg | 13.27 Ohm | 1.6 s | Quad | 10 Ohm | On | 40 Ohm | 10 deg | 2.7 Ohm | 84 deg | 4.27 Ohm | 0 s | 4.06 s | 84 deg | 8.32 Ohm | 0.4 s | 12.94 Ohm | [5 empty] | 84 deg | 10.99 ohm | 1.6 s |  | PUP | 0.1 s |  | POP | 0.15 s | 0.1 s | Off | Off | Off | Off | On | On | Off | Off | M2 | Off |  |  |  |  | On | 0.73 A | 3.6 A | 30% | 80% | On | 0 s | Off | Off | Non | On | Block | 1P | [16 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.179 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1P-3QKmuQg1MlHPY7ElDPJs6wpZuxCryWU1_mN8mpfng/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.180 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1MdZ6Enr6Y2q97JgUB9rThQurVRGjooKTns1xEaxtN7E/edit?usp=drive_link | 7SL87 | Setting Terpasang | [52 empty] | Setting Terpasang | [43 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.181 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/1wCwDFJw1G5416feNkOtOGu-M8US49ozY3izaUqroNSM/edit?usp=drive_link | GRL 200 | Setting Terpasang |  | 767011 | 500kV/DEP |  | On | 47.1 Ohm | 9.92 Ohm | 0.68 Ohm | 29.76 Ohm | 6.34 Ohm |  |  | Mho | 10 Ohm | On | 23 Ohm | 37 deg | 86 deg | 7.95 Ohm | 0 s | 86 deg | 12.24 Ohm | 0.4 s | 86 deg | 29.12 Ohm | 1.6 s | Quad | 10 Ohm | On | 23 Ohm | 37 deg | 7.93 Ohm | 86 deg | 20.68 Ohm | 0 s | 12.13 Ohm | 86 deg | 33.69 Ohm | 0.4 s | 28.62 Ohm | [5 empty] | 86 deg | 37.39 Ohm | 1.6 s |  | PUP | 0.1 s |  | POP | 0 s | 0.1 s | On | On | On | Off | On | On | Off | Off | Off | Off |  |  |  |  | On | 0.3 A | 3 A | 30% | 80% | On | 0 s | Off | Off | Non | On | Non | 1P | [16 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.182 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/1RfqRnc2Jhl0Y7bVuY9D3GW9iy9SNbg3jPmqU5fFCaAQ/edit?usp=drive_link | GRL 200 | Setting Terpasang |  | 767011 | 500kV/DEP |  | On | 47.1 Ohm | 9.92 Ohm | 0.68 Ohm | 29.76 Ohm | 6.34 Ohm |  |  | Mho | 10 Ohm | On | 23 Ohm | 37 deg | 86 deg | 7.95 Ohm | 0 s | 86 deg | 12.24 Ohm | 0.4 s | 86 deg | 29.12 Ohm | 1.6 s | Quad | 10 Ohm | On | 23 Ohm | 37 deg | 7.93 Ohm | 86 deg | 20.68 Ohm | 0 s | 12.13 Ohm | 86 deg | 33.69 Ohm | 0.4 s | 28.62 Ohm | [5 empty] | 86 deg | 37.39 Ohm | 1.6 s |  | PUP | 0.1 s |  | POP | 0 s | 0.1 s | On | On | On | Off | On | Off | Off | Off | Off | Off |  |  |  |  | On | 0.3 A | 3 A | 30% | 80% | On | 0 s | Off | Off | Non | On | Non | 1P | [16 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.183 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1RQQoBbTf6BB1zJJy3Tv0m3ZIQD7fQpwRUIMkuh2oK2w/edit?usp=drive_link | PCS-931 | Setting Terpasang | 500kV/100V | 2000/1 A |  | 1.955 Ohm | 0.175 Ohm | 5.864 Ohm | 1.219 Ohm | 2.026 Ohm | 1.219 ohm | 30.14 km |  | 0.2 A | 1 | 1 | 1 |  | 0.68 Ohm | -0.12 | 85 deg | 2.719 Ohm | 0 s | 2.719 Ohm | 0 s | 4.079 Ohm | 0.4 s | 4.079 Ohm | 0.4 s | 13.275 Ohm | 1.6 s | 13.275 Ohm | 1.6 s | 4.079 Ohm | Z2 and Z3 | PUTT |  |  | Enable | Disable |  |  | Disable | Enable | Disable | Disable | Disable | Not Active | [10 empty] | OCR/GFR |  |  | Setting Terpasang
PHT.184 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1RQQoBbTf6BB1zJJy3Tv0m3ZIQD7fQpwRUIMkuh2oK2w/edit?usp=drive_link | PCS-931 | Setting Terpasang | 500kV/100V | 2000/1 A |  | 1.955 Ohm | 0.175 Ohm | 5.864 Ohm | 1.219 Ohm | 2.026 Ohm | 1.219 ohm | 30.14 km |  | 0.2 A | 1 | 1 | 1 |  | 0.68 Ohm | -0.12 | 85 deg | 2.719 Ohm | 0 s | 2.719 Ohm | 0 s | 4.079 Ohm | 0.4 s | 4.079 Ohm | 0.4 s | 13.275 Ohm | 1.6 s | 13.275 Ohm | 1.6 s | 4.079 Ohm | Z2 and Z3 | PUTT |  |  | Enable | Disable |  |  | Disable | Enable | Disable | Disable | Disable | Not Active | [10 empty] | OCR/GFR |  |  | Setting Terpasang

## HEL_PHT_TAP (hidden)
ID | SEGMEN A | SEGMEN B | SRC | TIPE | LISTING
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140
| https://docs.google.com/spreadsheets/d/1Q4nu_sbz6U1WAX2ht5Fa3gfWAyQjgaPO4IfotxhTj9k/edit?resourcekey=&gid=995590498#gid=995590498 |  | https://docs.google.com/spreadsheets/d/1ZKPej-AGG0QtAnPVT1f1-UdGKVZ6JPwo-SlTcIef0Cw/edit?usp=drive_link | MICOM P545 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P546 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P543 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P521 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail | Supervision | System Check | Autoreclose |  | Parameter | CT | VT | Line Length | Line Impedance | Line Angle | kZN Res Comp | kZN Res Angle | Current Diff | Phase Is1 | Phase Is2 | Phase k1 | Phase k2 | Phase Time Delay | Transient Bias | In Diff | Delta I2 | Delta i1 | Start I2 | Start I1 | [5 empty] | Scheme Logic | tZ1 Ph. Delay | tZ2 Ph. Delay | tZ3 Ph. Delay | Aid 1 Selection | tRev Guard | Aid 2 Selection | tRev Guard | SOTF Status | SOTF Tripping | TOR Status | TOR Tripping | ISEF Start (Blocking) | Superviion | VTS Mode | CTS Mode | Idiff Supervision | Dist. Element | Z1 Ph. Reach | Z1 Ph. Angle | R1 Ph. Resistive | Z2 Ph. Reach | Z2 Ph. Angle | R2 Ph. Resistive | Z3 Ph. Reach | Z3 Ph. Angle | R3 Ph. Resistive | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Live Line | Dead Line | Sys Checks CB1 | CB1 CS Volt. Blk | CB1 CS1 Status | CB1 CS1 Angle | CB1 Vdiff | CB1 CS1 SlipFreq |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Tap Setting 30/08/2022 | [6 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1qTIqpv3M4b7ZRFh1Fll3GEGWXwiKFHTKElCF1MX9Cx0/edit?gid=544152550#gid=544152550 | MICOM P443 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail and I< | Supervision | System Check | Autoreclose |  | Parameter | Phase CT Primary | Main VT Primary | Distance Element | Line Length | Line Impedance | Line Angle | kZ Res Comp | kZ Res Angle | Z1 | R1G | R1Ph | tZ1 | Z2 | R2G | R2Ph | tZ2 | Z3 | R3G | R3Ph | tZ3 |  |  |  |  | Distance Scheme | Program Mode | Standard Mode | Aid Dist. Dly | tReversal Guard | Unblocking Logic | SOTF/TOR Mode | SOTF Delay | Z1Ext Fail | Power Swing | Delta R | Delta X | IN> Status | Superviion | VTS Mode | CTS Mode | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Chk scheme A/R | C/S Sheck Scheme for Man CB | V<Dead Line | V<Live Line | V<Dead Bus | V<Live Bus | Diff Voltage | Diff Frequency | Diff Phase |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [16 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 20-01-2022 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P442 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail and I< | Supervision | System Check | Autoreclose |  | Parameter | Phase CT Primary | Main VT Primary | Distance Element | Line Length | Line Impedance | Line Angle | kZ Res Comp | kZ Res Angle | Z1 | R1G | R1Ph | tZ1 | Z2 | R2G | R2Ph | tZ2 | Z3 | R3G | R3Ph | tZ3 |  |  |  |  | Distance Scheme | Program Mode | Standard Mode | Aid Dist. Dly | tReversal Guard | Unblocking Logic | SOTF/TOR Mode | SOTF Delay | Z1Ext Fail | Power Swing | Delta R | Delta X | IN> Status | Superviion | VTS Mode | CTS Mode | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Chk scheme A/R | C/S Sheck Scheme for Man CB | V<Dead Line | V<Live Line | V<Dead Bus | V<Live Bus | Diff Voltage | Diff Frequency | Diff Phase |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [16 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 20-01-2022 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  |  | MICOM P446 | Parameter | Configuration | Setting Group 1 | Distance | Directional E/F | Current Diff | Overcurrent | Neg Sequence O/C | Broken Conductor | Earth Fault | SEF/REF Prot'n | Residual O/V NVD | Thermal Overload | Power Swing Block | Volt Protection | Freq Protection | CB Fail and I< | Supervision | System Check | Autoreclose |  | Parameter | Phase CT Primary | Main VT Primary | Distance Element | Line Length | Line Impedance | Line Angle | kZ Res Comp | kZ Res Angle | Z1 | R1G | R1Ph | tZ1 | Z2 | R2G | R2Ph | tZ2 | Z3 | R3G | R3Ph | tZ3 |  |  |  |  | Distance Scheme | Program Mode | Standard Mode | Aid Dist. Dly | tReversal Guard | Unblocking Logic | SOTF/TOR Mode | SOTF Delay | Z1Ext Fail | Power Swing | Delta R | Delta X | IN> Status | Superviion | VTS Mode | CTS Mode | Autoreclose | AR Mode | Multi Phase AR | Discrim Time | SP AR Dead Time | 3P AR DT Shot 1 | System Checks | Chk scheme A/R | C/S Sheck Scheme for Man CB | V<Dead Line | V<Live Line | V<Dead Bus | V<Live Bus | Diff Voltage | Diff Frequency | Diff Phase |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [16 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 20-01-2022 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/15M9aJzZzNu5hlgrMke4A-x8s0Bqc0Sw3YQzyredDJcI/edit?usp=drive_link | L90 | Parameter | AC Inputs | Current | Voltage | Grouped Element/Group 1 | Current Differential | Function | Pickup | Restrain 1 | Restrain 2 | Breakpoint | 87L Current Diff Gnd Function | Stub Bus | Line Pickup | Function | Phase IOC Line Pickup | UV Pickup | Phase Distance | Phase Distance Z1 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Phase Distance Z2 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | [5 empty] | Parameter | Phase Distance Z3 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Ground Distance Z1 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Ground Distance Z2 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | Ground Distance Z3 | Reach | RCA | Comp Limit | DIR RCA | DIR Comp Limit | Quad Right Blinder | Quad Right Blinder RCA | Quad Left Blinder | Quad Left Blinder RCA | Delay | [5 empty] | Parameter | Power Swing Detect | Load Encroachment | Phase Current | Phase TOC | Phase IOC | Phase Directional | Neutral Current | Neutral IOC | Phase IOC | Neutral Directional IOC | Transient Ground Fault | Wattmetric Ground Fault | Ground Current | Ground TOC | Ground IOC | Negative Sequence Current | Negative Sequence TOC | Negative Sequence IOC | Negative Sequence Directional | Breaker Failure | Voltage Element | Supervising Element | Disturbance Detector | 87L Trip | Underfrequency | Overfrequency | Thermal Overload Prot | Pilot Scheme |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | Jenis Relay | Tipe Relay | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1x8x8zV4t51Gk41JCc78MVuYC3wnSzjAg3csMLBbGVL8/edit?usp=drive_link | 7SL87 | Parameter | CT | VT | General | C1 Per Length | C0 Per Length | X Per Length | Kr / Kx | Line Length | Line Angle | 87 Line Differential | I-DIFF | Threshold | Operate Delay | I-DIFF Fast | Threshold | IC-Compensation | Mes. V failure | Mode | Asym. Fail. -time delay | 68 P.swing | Zones to be blocked | 50/51 O/C Gnd -A | Mode | 21 Distance Prot. | Dist. Characteristic Angle | Z1 | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z2 | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z3 | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z1 (Mho) | X Reach | R (Ph-g) | R (Ph-ph) | Operate Delay | Z2 (Mho) | X Reach | [5 empty] | Parameter | R (Ph-g) | R (Ph-ph) | Z3 (Mho) | X Reach | R (Ph-g) | R (Ph-ph) | 50 OC highspeed | Switch onto Fault | Configuration | Mode | Operate Delay | Aided Scheme | Send With | Operate With | Mode | Send prolongation |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 14-12-2018 | [23 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : Tap Setting 12-07-2018 |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [9 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1HmSu_VUPIme2KvbscEGPdfpsM5rONe6A_eINQFARbH4/edit?usp=drive_link | 7SD61 | Parameter | CT | VT | General | C1 Per Length | C0 Per Length | X Per Length | Kr / Kx | Line Length | Line Angle | 87 Line Differential | I-DIFF | Threshold | Operate Delay | I-DIFF Fast | Threshold | IC-Compensation | Mes. V failure | Mode | Asym. Fail. -time delay |  |  | 50/51 O/C Gnd -A | Mode |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [18 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1X6YT1INoslajhA2bTFUi7EPXzoylquoFS_azi6Oih8Q/edit?usp=drive_link | RED670 | Parameter | CT | VT | Diff Mode | IdMin | EndSection1 | EndSection2 | SlopeSection2 | SlopeSection3 | IdMinHigh | tIdMinHigh | I2/I1Ratio | I5/I1Ratio | OpenCTEnable | tOCTResetDelay | LossSynEn | Setting Group 1 | RLdFw | RLdFwMax | RLdFwMin | RStart | XStart | ArgLd | ArgDir | ArgNegRes | Zone 1 | tPP | X1PPZ1 | R1PPZ1 | X1PEZ1 | X1PEZ1 | X0Z1 | R0Z1 | RFPPZ1 | RFPEZ1 | tPPZ1 | Zone 2 | X1Z2 | R1Z2 | X0Z2 | R0Z2 | [5 empty] | Parameter | RFPPZ2 | RFPEZ2 | tPPZ2 | Zone 3 | X1Z3 | R1Z3 | X0Z3 | R0Z3 | RFPPZ3 | RFPEZ3 | tPPZ3 | Automatic SOTF | Operation | AutoInitMode | Power Swing Detection | Operation | Fault Locator | R1A | X1A | R1B | X1B | R1L | X1L | R0L | X0L | LineLength | Scheme Communication | SchemeType | tSecurity | Current Protection | EF4PTOC : 1 | Operation | DirMode1 | Fuse Failure | Operation | OpMode | Autorecloser | Operation | CBReady Tpe | t1 1Ph | t1 3Ph | Synchronizing | OperationSynch |  |  |  |  | Parameter | UDiff Synch | FreqDiffMax | CloseAngleMax |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | Ie> | tms | Ie>> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) |  | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/1bG5rOiNz_-liuI3ZWq6e9w0Pvo9SQmXx2tLZR0kWhyU/edit?usp=drive_link | PCS-931 | Parameter | U1n/U2n | I1n_Base/I2n_Base | Line Setting | X1L | R1L | X0L | R0L | X0M | R0M | Line Length | Diff Setting | 87L.I_Pkp | 87L.K_Cr_CT | 87L.En | 87L.En_Neutral | Dist Setting | 21-1.Real_k0 | 21-1.Imag_k0 | 21-1.phi1_Reach | 21M1.ZG.Z_Set | 21M1.ZG.t_Op | 21M1.ZP.Z_Set | 21M1.ZP.t_Op | 21M2.ZG.Z_Set | 21M2.ZG.t_Op | 21M2.ZP.Z_Set | 21M2.ZP.t_Op | 21M3.ZG.Z_Set | 21M3.ZG.t_Op | 21M3.ZP.Z_Set | 21M3.ZP.t_Op | 21M.Pilot.Z_Set | 21M.PSBR (silangi yang tidak bernilai 1) | 85.Opt_PilotMode | Additional | 50/51Gx.En | 21SOTF.En | 78.En_Trp (OOS) | 50/51G1.En/sejenisnya | 50/51P1.En/sejenisnya | 85.DEF.En | VTS.En | CB1.25.En_SynChk | CB1.25.En_NoChk | CB1.79.En | AR Mode |  |  |  |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  |  | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) |  | Tap Setting No :
|  |  | https://docs.google.com/spreadsheets/d/19botCaaavxDBaf-vARrZlUhyojcuz9Rbbh_3pnyAtjE/edit?usp=drive_link | GRL 200 | Parameter | Analog Input | CT | VT | Fault Locator | FL_EN | FL_1Line_km | FL_1X1 | FL_1R1 | FL_1X0 | FL_1R0 |  | Distance | ZS-Chara | PSBSZ | LES-EN | LESR | LESR-Angle | Z1S-Mho.Angle | Z1S-Mho.Reach | TZ1S | Z2S-Mho.Angle | Z2S-Mho.Reach | TZ2S | Z3S-Mho.Angle | Z3S-Mho.Reach | TZ3S | ZG-Chara | PSBGZ | LEG-EN | LEGR | LEGR-Angle | Z1G-X.Reach | Z1G-R.Angle | Z1G-R.Reach | TZ1G | Z2G-X.Reach | Z2G-R.Angle | Z2G-R.Reach | TZ2G | Z3G-X.Reach | [5 empty] | Z3G-R.Angle | Z3G-R.Reach | TZ3G | Carrier Distance | Dis-CAR | TREBK-Dis | Carrier DEF | DEF-CAR | TDEFCF | TREBK-DEF | EF | EF1-EN | EF2-EN | SOTFOC-EN | VTF1-EN | CTF-EN | ARC1-EN | ARC1-MODE | MPAR-MODE | ARC1-VCHK-EN | SYN1-dV | SYN1-dfEN | SYN1-df | Differential | DIFL_EN | DIFL-I1 | DIFL-I2 | DIFL-Slope 1 | DIFL-Slope 2 | DIFL-IcC.En | TDIFL | DIFL-RDIF-EN | DIFL-IdSV-EN | DIFL-CTFBlk | DIFLFS-EN | DIFL-ARCBlk | DIFL-TPMD |  |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : | [11 empty] | Jenis Relay | Tipe Relay |  | Parameter | CT | *OCR | I> | tms | I>> | tms | *GFR | I> | tms | I> | tms | CTS Enabled | CB Fail |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan : |  |  | Parameter "OCR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51P1 atau 50/51P4 atau lain-lain (menyesuaikan) |  | Parameter "GFR" diisikan sesuai dengan elemen yang aktif pada relay yang terpasang: | a. NR : 50/51G1 atau 50/51G2 atau lain-lain (menyesuaikan) | [6 empty] | Tap Setting No :
PHT.01 | ANGKE | ANCOL | https://docs.google.com/spreadsheets/d/1_feMC27xQFEnCmytl4JDOBOWFZPWBcca_pqeWjEp_Wc/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 2000 / 5 A | 150 kV / 100 V | 4.6 km | 0.329 ohm | 70.066 deg | 0.654 | 3.382 deg |  | 1 A | 10 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | PUR | 100 ms | Disabled |  | Enable Pole Dead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | I Diff |  |  | 0.263 ohm | 70.066 deg | 5.46 ohm | 0.403 ohm | 70.066 deg | 6.06 ohm | 0.951 ohm | 70.066 deg | 6.74 ohm |  | 1PAR/3PAR | BAR 3 Phase | 100 ms | 1 s | 3 s |  | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.02 | ANGKE | ANCOL | https://docs.google.com/spreadsheets/d/1ZKPej-AGG0QtAnPVT1f1-UdGKVZ6JPwo-SlTcIef0Cw/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 2000 / 5 A | 150 kV / 100 V | 4.6 km | 0.329 ohm | 70.066 deg | 65.4% | 3.382 deg |  | 1 A | 10 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | PUR | 100 ms | Disabled |  | Enable Pole Dead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | I Diff |  |  | 0.263 ohm | 70.066 deg | 5.46 ohm | 0.403 ohm | 70.066 deg | 6.06 ohm | 0.951 ohm | 70.066 deg | 6.74 ohm |  | 1PAR/3PAR | BAR 3 Phase | 100 ms | 1 s | 3 s |  | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.03 | ANGKE | KARET LAMA | https://docs.google.com/spreadsheets/d/1qTIqpv3M4b7ZRFh1Fll3GEGWXwiKFHTKElCF1MX9Cx0/edit?gid=544152550#gid=544152550 | MICOM P443 | Tap Setting | [20 empty] | Tap Setting | [79 empty] | Tap Setting | 767132 |  | 3.75 A | 0.373 SI | Disabled | - |  | 0.625 A | 0.659 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.04 | ANGKE | KARET LAMA | https://docs.google.com/spreadsheets/d/1qj6Lzay1QbYrp03gjdLecJRnw8A2fSOiQGGwjEc1-RE/edit?usp=drive_link | MICOM P443 | Tap Setting | [20 empty] | Tap Setting | [79 empty] | Tap Setting | 767132 |  | 3.75 A | 0.373 SI | Disabled | - |  | 0.625 A | 0.659 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.05 | ANGKE | KETAPANG | https://docs.google.com/spreadsheets/d/1MGuDnJQjAXaXIgYMsUYepUsSRu-UBFbbFhzmkb2QyWs/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 500 / 5 | 150 / 100 | 5.5 km | 0.064 ohm | 56.6 deg | 0.64 | 3.8 deg |  | 1 A | 10 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | Measured+MCB | Disabled | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | [5 empty] | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 500 / 5 |  | 6 A | 0.608 SI | Disabled | - |  | 1 A | 0.879 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.06 | ANGKE | KETAPANG | https://docs.google.com/spreadsheets/d/185vGIM_krvzVjYEP75fefF7QNys4Z1ciW9-THtsqxIU/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 500 / 5 | 150 / 100 | 5.5 km | 0.064 ohm | 56.6 deg | 64% | 3.8 deg |  | 1 A | 10 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | Measured+MCB | Disabled | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | [5 empty] | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 500 / 5 |  | 6 A | 0.608 SI | Disabled | - |  | 1 A | 0.879 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.07 | ANGKE | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1HmSu_VUPIme2KvbscEGPdfpsM5rONe6A_eINQFARbH4/edit?usp=drive_link | 7SD61 | Tap Setting | 2000 / 5 A | 150 kV / 100 V |  | 18,81 uF/km | 18,81 uF/km | 0,468 ohm/km | 1,385 / 0,667 | 3,6 km | -57,296 deg |  | ON | 1 A (0,2xIn) | 0 s | ON | 10 A (2xIn) | ON |  | OFF | - |  |  |  | OFF | [25 empty] | Tap Setting | 2000 / 5 A |  | 3.6 A | 0.527 SI | Disabled | - |  | 0.6 A | 0.846 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.08 | ANGKE | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/117KSkWV1SUcCvwWvQBe-7qtydrWoDf3LTLqZ-cRBxKc/edit?usp=drive_link | 7SD61 | Tap Setting | 2000 / 5 A | 150 kV / 100 V |  | 18,81 uF/km | 18,81 uF/km | 0,468 ohm/km | 1,385 / 0,667 | 3,6 km | -57,296 deg |  | ON | 1 A (0,2xIn) | 0 s | ON | 10 A (2xIn) | ON |  | OFF | - |  |  |  | OFF | [25 empty] | Tap Setting | 2000 / 5 A |  | 3.6 A | 0.48 SI | Disabled | - |  | 0.6 A | 0.75 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.09 | ANGKE | UGC MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1x8x8zV4t51Gk41JCc78MVuYC3wnSzjAg3csMLBbGVL8/edit?usp=drive_link | 7SL87 | Tap Setting | 2000-05-01 | 150kV/100V |  | 0.47 uF/km | 0.47 uF/km | 0.125 ohm/km | 1.385/0.667 | 3.6 km | 81.357 deg |  | On | 1 A | 0 s | On | 10 A | On |  | - | - |  | - |  | Disabled | Off | - |  | - | - | - | - |  | - | - | - | - |  | - | - | - | - |  | - | - | - | - |  | - | [5 empty] | Tap Setting | - | - |  | - | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 2000-05-01 |  | 5.25 A | 0.43 SI | Disabled | - |  | 0.875 A | 0.522 SI | Disabled | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.10 | ANGKE | UGC MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1DaMcxhO1EMx3VFiwcgC0WLlbavsPToE4IZhuJotgdj0/edit?usp=drive_link | 7SL87 | Tap Setting | 2000-05-01 | 150kV/100V |  | 0.47 uF/km | 0.47 uF/km | 0.125 ohm/km | 1.385/0.667 | 3.6 km | 81.357 deg |  | On | 1 A | 0 s | On | 10 A | On |  | - | - |  | - |  | Disabled | Off | - |  | - | - | - | - |  | - | - | - | - |  | - | - | - | - |  | - | - | - | - |  | - | [5 empty] | Tap Setting | - | - |  | - | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 2000-05-01 |  | 5.25 A | 0.43 SI | Disabled | - |  | 0.875 A | 0.522 SI | Disabled | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.11 | DADAP | LONTAR | https://docs.google.com/spreadsheets/d/1zb-AMDz1Y4yx4LJ4kQxYhfEuYM5_UQ_h1MXrHngQqOk/edit?usp=drive_link | MICOM P446 | Tap Setting |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V |  | 25,588 km | 19,398 ohm | 82,725 deg | 0.684 | -7.618 | 15,519 ohm | 34,26 ohm | 34,26 ohm | 0 s | 25,819 ohm | 38,07 ohm | 38,07 ohm | 0,4 s | 42,591 ohm | 42,3 ohm | 42,3 ohm | [11 empty] | Enabled | 30 s | [6 empty] | Measured + MCB | Disabled |  | 1PAR/3PAR | [5 empty] | 1/3 PAR | Enabled | 11,5 V | 52 V | 11,5 V | 52 V | 6 V | 0,167 Hz | 15 deg | [23 empty] | Tap Setting | 4000/1 A |  | 0,819 A (sec) | 0,269 (SI) | - | - |  | 0,137 A (sec) | 0,531 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.12 | DADAP | LONTAR | https://docs.google.com/spreadsheets/d/1WVN2za7lQTd2VIPIs-tTixzcZxSU8MZTMqM7oTBrCr8/edit?usp=drive_link | MICOM P446 | Tap Setting |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V |  | 25,588 km | 19,398 ohm | 82,725 deg | 0.684 | -7.618 | 15,519 ohm | 34,26 ohm | 34,26 ohm | 0 s | 25,819 ohm | 38,07 ohm | 38,07 ohm | 0,4 s | 42,591 ohm | 42,3 ohm | 42,3 ohm | [11 empty] | Enabled | 30 s | [6 empty] | Measured + MCB | Disabled |  | 1PAR/3PAR | [5 empty] | 1/3 PAR | Enabled | 11,5 V | 52 V | 11,5 V | 52 V | 6 V | 0,167 Hz | 15 deg | [23 empty] | Tap Setting | 4000/1 A |  | 0,819 A (sec) | 0,269 (SI) | - | - |  | 0,137 A (sec) | 0,531 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.13 | DADAP | TELUK NAGA | https://docs.google.com/spreadsheets/d/1_7zzuc3kqP8gs0-RvMQZqs__EvVgSALJYksmlBl7RXU/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V | 6,132 km | 4,649 ohm | 82,725 deg | 0.684 | -7.168 |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 3,719 ohm | 82,725 deg | 34,26 ohm | 8,15 ohm | 82,725 deg | 38,07 ohm | 13,887 ohm | 82,725 deg | 42,3 ohm |  | 1PAR/3PAR | - | - | - | - |  | 52V | 11,5V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 4000/1A | Group 1 | 0,819 A (sec) | 0,269(SI) | - | - | Group 1 | 0,137 A (sec) | 0,531(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.14 | DADAP | TELUK NAGA | https://docs.google.com/spreadsheets/d/1UBstAMlW87TlYf7d0kKptpIhB2xdTGBqKn6_ih40fMc/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V | 6,132 km | 4,649 ohm | 82,725 deg | 0.684 | -7.168 |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 3,719 ohm | 82,725 deg | 34,26 ohm | 8,15 ohm | 82,725 deg | 38,07 ohm | 13,887 ohm | 82,725 deg | 42,3 ohm |  | 1PAR/3PAR | - | - | - | - |  | 52V | 11,5V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 4000/1A | Group 1 | 0,819 A (sec) | 0,269(SI) | - | - | Group 1 | 0,137 A (sec) | 0,531(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.15 | MUARAKARANG BARU | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1VxGLKtNFrq3w9160PxX92v0ZfUJC78lcZZT4I8wEaSo/edit?usp=sharing | MICOM P545 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | 219268 | 50/51P4 | 4.8 A | 0.469 SI | - | - | 50/51G4 | 0.8 A | 0.808 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.16 | MUARAKARANG BARU | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/14NcijQiUUUrJNgxaXrzHMIV1i8qESxkADZbLcfES6KY/edit?usp=sharing | MICOM P545 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | 219268 | 50/51P4 | 4.8 A | 0.469 SI | - | - | 50/51G4 | 0.8 A | 0.808 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.17 | MUARAKARANG BARU | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/1CHCZRetMGgeFImQEF7NwZNsFlRUGwfJ-bQn8Or5-20o/edit?usp=drive_link | MICOM P521 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.18 | MUARAKARANG BARU | MUARAKARANG LAMA | https://docs.google.com/spreadsheets/d/17jLKzetQ5moSvleindl6n0VJnd_pB_bBMhqmPA0ccus/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Disabled | Disabled | Enabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 4000 / 5 A | 150 kV / 100 V | 0.7 km | 0.2 ohm | 82 deg | 0.68 | -7 deg |  | 1.5 A | 5 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | Measured + MCB | IDiff+Std | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.19 | MUARAKARANG LAMA | ANGKE | https://docs.google.com/spreadsheets/d/1bU3CdLZuuvrfJQ9RiGxwRfx0ck10eRFG9B1VYpZvYCU/edit?usp=drive_link | 7SD61 | Tap Setting | 2000 / 5 A | 150 kV / 100 V |  | 18,81 uF/km | 18,81 uF/km | 0,468 ohm/km | 1,385 / 0,667 | 3,6 km | -57,296 deg |  | ON | 1 A (0,2xIn) | 0 s | ON | 10 A (2xIn) | ON |  | OFF | - |  |  |  | OFF | [25 empty] | Tap Setting | 2000 / 5 A |  | 5,25 A | 0,45 SI | Disabled | - |  | 0,875 A | 0,79 SI | Disabled | - | [19 empty] | Tap Setting Tanggal
PHT.20 | MUARAKARANG LAMA | ANGKE | https://docs.google.com/spreadsheets/d/1YPIrB_myuVj18UC9n3sQMVCPOFOWGoNdFJUiSzP21ZU/edit?usp=drive_link | 7SD61 | Tap Setting | 2000 / 5 A | 150 kV / 100 V |  | 18,81 uF/km | 18,81 uF/km | 0,468 ohm/km | 1,385 / 0,667 | 3,6 km | -57,296 deg |  | ON | 1 A (0,2xIn) | 0 s | ON | 10 A (2xIn) | ON |  | OFF | - |  |  |  | OFF | [25 empty] | Tap Setting | 2000 / 5 A |  | 5,25 A | 0,45 | Disabled | - |  | 0,875 A | 0,79 | Disabled | - | [19 empty] | Tap Setting Tanggal
PHT.21 | MUARAKARANG LAMA | BUDIKEMULYAN | https://docs.google.com/spreadsheets/d/1yexP-aydoUDEUEuEoWyp19xlAZ0COr0NnYs18Osgp_U/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Group 1 | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 150kV/100V | 1200/5 A | 14 km | 0.26 ohm | 72.87 deg | 0.772 | -17.235 deg |  | 0.61 A | 6.13 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 0.21 ohm | 72.87 deg | 6.61 ohm | 0.31 ohm | 72.87 deg | 7.35 ohm | 0.43 ohm | 72.87 deg | 8.16 ohm |  | Not Active | - | - | - | - |  | - | - | Disabled | - | - | - | - | - | [14 empty] | Tap Setting | 1200 / 5 A |  | 3,675 A (sec) | 0,628 (IEC Norm Inv) | Disabled | - |  | 0,615 A (sec) | 0,975 (IEC Norm Inv) | Disabled | - | [19 empty] | Tap Setting Tanggal
PHT.22 | MUARAKARANG LAMA | BUDIKEMULYAN | https://docs.google.com/spreadsheets/d/1Pb8of-UR7UstAUi76PlEND2272bwV-msDOVxiUp8STY/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Group 1 | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 150kV/100V | 1200/5 A | 14 km | 0.26 ohm | 72.87 deg | 0.772 | -17.235 deg |  | 0.61 A | 6.13 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 0.21 ohm | 72.87 deg | 6.61 ohm | 0.31 ohm | 72.87 deg | 7.35 ohm | 0.43 ohm | 72.87 deg | 8.16 ohm |  | Not Active | - | - | - | - |  | - | - | Disabled | - | - | - | - | - | [14 empty] | Tap Setting | 1200 / 5 A |  | 3,675 A (sec) | 0,628 (IEC Norm Inv) | Disabled | - |  | 0,615 A (sec) | 0,975 (IEC Norm Inv) | Disabled | - | [19 empty] | Tap Setting Tanggal
PHT.23 | MUARAKARANG LAMA | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1S2rihWhXy3w5Ww6MHGm6lgCA6W9oU9y_iOhuo-TucH0/edit?usp=drive_link | MICOM P521 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | 2000/5 A |  | 1 In | 0.541 SI | - | - |  | 0.167 In | 0.804 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.24 | MUARAKARANG LAMA | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1fJKaIBpjVeSkgeh6v32tj35e4KKG3b6u9m04JV_aELA/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Disabled | Disabled | Enabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  | Tap Setting | 2000 / 5 A | 150 kV / 100 V | 0.7 km | 0.2 ohm | 82 deg | 0.68 | -7 deg |  | 3 A | 5 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000/5 A |  | 1 In | 0.541 SI | - | - |  | 0.167 In | 0.804 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.25 | MUARAKARANG LAMA | UGC ANGKE | https://docs.google.com/spreadsheets/d/1rbyqufWMloGUbWyrpwEyPX_u-cHww-6bFaYKw-T3Rt0/edit?usp=drive_link | 7SL87 | Tap Setting | 2000 / 5 A | 150 kV / 100 V |  | 0,47 uF/km | 0,47 uF/km | 0,125 ohm/km | 1,385 / 0,667 | 3,6 km | 81,357 deg |  | ON | 1 A (0,2xIn) | 0 s | ON | 10 A (2xIn) | ON |  | OFF | - | OFF | - |  | OFF | OFF | [28 empty] | Tap Setting | [46 empty] | Tap Setting | 2000 / 5 A |  | 5,25 A | 0,45 | Disabled | - |  | 0,875 A | 0,79 | Disabled | - | [22 empty] | Tap Setting Tanggal
PHT.26 | MUARAKARANG LAMA | UGC ANGKE | https://docs.google.com/spreadsheets/d/1GhA89opUsE6DY2sgNZ1_11q9NqUSkgCehakKWigHir4/edit?usp=drive_link | 7SL87 | Tap Setting | 2000 / 5 A | 150 kV / 100 V |  | 0,47 uF/km | 0,47 uF/km | 0,125 ohm/km | 1,385 / 0,667 | 3,6 km | 81,357 deg |  | ON | 1 A (0,2xIn) | 0 s | ON | 10 A (2xIn) | ON |  | OFF | - | OFF | - |  | OFF | OFF | [28 empty] | Tap Setting | [46 empty] | Tap Setting | 2000 / 5 A |  | 5,25 A | 0,45 | Disabled | - |  | 0,875 A | 0,79 | Disabled | - | [22 empty] | Tap Setting Tanggal
PHT.27 | DAAN MOGOT | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1X6YT1INoslajhA2bTFUi7EPXzoylquoFS_azi6Oih8Q/edit?usp=drive_link | RED670 | Tap Setting | 3000/1 A | 150 kV/100 V |  | 0,2 x Ibase | 1,25 x Ibase | 2 x Ibase | 30% | 80% | 1 x Ibase | 1 s | 15% | 30% | Off | 0,01 s | - | [10 empty] | 0 s | 2,073 ohm | 0,316 ohm | 2,073 ohm | 0,316 ohm | 6,219 ohm | 0,568 ohm | 4,354 ohm | 15,623 ohm | 0 s |  | 3,11 ohm | 0,474 ohm | 9,329 ohm | 0,852 ohm | [5 empty] | Tap Setting | 6,53 ohm | 22,319 ohm | 0,4 s |  | 22,212 ohm | 3,384 ohm | 36,219 ohm | 36,219 ohm | 46,645 ohm | 31,884 ohm | 1,6 s |  | On | Off |  | On | [6 empty] | 2.591 ohm |  |  | 2,63 km | [5 empty] | Off | - |  |  |  |  | On |  | 1 s |  |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting; tms: 3000/1 A; I>: 1,006 A; tms: 0.335; I>: -; tms: - |  | 0,168 A | 0.619 | - | - | - | - | [10 empty] | Tap Setting Tanggal
PHT.28 | DAAN MOGOT | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1G3gsiHGK3LZk-LYVkMn4Lp_b20qWblsNuM-mr210khk/edit?usp=drive_link | RED670 | Tap Setting | 3000/1 A | 150 kV/100 V |  | 0,2 x Ibase | 1,25 x Ibase | 2 x Ibase | 30% | 80% | 1 x Ibase | 1 s | 15% | 30% | Off | 0,01 s | - | [10 empty] | 0 s | 2,073 ohm | 0,316 ohm | 2,073 ohm | 0,316 ohm | 6,219 ohm | 0,568 ohm | 4,354 ohm | 15,623 ohm | 0 s |  | 3,11 ohm | 0,474 ohm | 9,329 ohm | 0,852 ohm | [5 empty] | Tap Setting | 6,53 ohm | 22,319 ohm | 0,4 s |  | 22,212 ohm | 3,384 ohm | 36,219 ohm | 36,219 ohm | 46,645 ohm | 31,884 ohm | 1,6 s |  | On | Off |  | On | [6 empty] | 2,591 ohm |  |  | 2,63 km | [5 empty] | Off | - |  |  |  |  | On |  | 1 s |  |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting; tms: 3000/1 A; I>: 1,006 A; tms: 0.335; I>: -; tms: - |  | 0,168 A | 0.619 | - | - | - | - | [10 empty] | Tap Setting Tanggal
PHT.29 | DAAN MOGOT | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1nF3Yb-cxvss-mTzXAisCXpRT-x9d3h7daUeEVFqLyfs/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 3000/1 A | 150kV/100V | 4,6 km | 11,484 ohm | 81,3 deg | 0.66 | 5,2 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Blocking | 0 s | Disabled | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 9,187 ohm | 81,338 deg | 21,16 ohm | 16,696 ohm | 81,338 deg | 26,46 ohm | 27,861 ohm | 81,338 deg | 33,07 ohm |  | 1PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 3000/1 A |  | 1,006 A | 0,335 (SI) | - | - |  | 0,168 A | 0,619 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.30 | DAAN MOGOT | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1b8Ar6yu7d-JedzfZhqR2BYpxHEu0SyHQUtRoaXE3dck/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 3000/1 A | 150kV/100V | 4,6 km | 11,484 ohm | 81,3 deg | 0.66 | 5,2 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Blocking | 0 s | Disabled | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 9,187 ohm | 81,338 deg | 21,16 ohm | 16,696 ohm | 81,338 deg | 26,46 ohm | 27,861 ohm | 81,338 deg | 33,07 ohm |  | 1PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 3000/1 A |  | 1,006 A | 0,335 (SI) | - | - |  | 0,168 A | 0,619 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.31 | GROGOL | GROGOL BARU | https://docs.google.com/spreadsheets/d/1Uj1gPjF81B0mSfMFdXGmpnwtd063LYrSFByThhgI600/edit?usp=drive_link | 7SL87 | Tap Setting | 1600/1A | 150kV/100V |  | 0,016 uF/km | 0,016 uF/km | 0,299 ohm/km | 1,29 / 0,67 | 2 km | 82 deg |  | On | 0,2 A (0,2xIn) | 0 | On | 2 A | On |  | On | 10 s | [7 empty] | 0,479 ohm | 23 ohm |  | 0 s |  | 1,718 ohm | 25 ohm |  | 0,4 s |  | 3,043 ohm | 28 ohm |  | 1,6 s | [12 empty] | Tap Setting | [9 empty] | On | 3 s | [35 empty] | Tap Setting | 1600/1A |  | 1,2 A | 0,290(SI) | - | - |  | 0,2 A (sec) | 0,586(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.32 | GROGOL | GROGOL BARU | https://docs.google.com/spreadsheets/d/1zEZexc5bkP17UqfqRgeoSB6PBIt_OpVXjYJdxr3rCqc/edit?usp=drive_link | 7SL87 | Tap Setting | 1600/1A | 150kV/100V |  | 0,016 uF/km | 0,016 uF/km | 0,299 ohm/km | 1,29 / 0,67 | 2 km | 82 deg |  | On | 0,2 A (0,2xIn) | 0 | On | 2 A | On |  | On | 10 s | [7 empty] | 0,479 ohm | 23 ohm |  | 0 s |  | 1,718 ohm | 25 ohm |  | 0,4 s |  | 3,043 ohm | 28 ohm |  | 1,6 s | [12 empty] | Tap Setting | [9 empty] | On | 3 s | [35 empty] | Tap Setting | 1600/1A |  | 1,2 A | 0,42(SI) | - | - |  | 0,2 A | 0,68(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.33 | GROGOL | TOMANG | https://docs.google.com/spreadsheets/d/16KyrtoLa4_wA5ncdvK-LACsFt6b4ckA0XP5vGzG2xwg/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Disabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,11 km | 0,831 ohm | 85 deg | 0.263 | 26 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,664 ohm | 85 deg | 39 ohm | 1,148 ohm | 85 deg | 43 ohm | 2,38 ohm | 85 deg | 48 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,715 A | 0,4(SI) | - | - | Group 1 | 0,120 A | 0,674(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.34 | GROGOL | TOMANG | https://docs.google.com/spreadsheets/d/15gmDhpZ_XTW0_Zka9m91Wvf9hcZFQWeeC1JR6TXVxzE/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Disabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,11 km | 0,831 ohm | 85 deg | 0.263 | 26 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,664 ohm | 85 deg | 39 ohm | 1,148 ohm | 85 deg | 43 ohm | 2,38 ohm | 85 deg | 48 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,715 A | 0,4(SI) | - | - | Group 1 | 0,120 A | 0,674(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.35 | GROGOL BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1TSpR3FNKHwccw-h73vjdljseZHj5xabxDaJdJMCM3zY/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/1A | 150kV/100V |  | 0,016 uF/km | 0,016 uF/km | 0,374 ohm/km | 1,29 / 0,67 | 6,468 km | 82 deg |  | On | 0,2 A (0,2xIn) | 0 | On | 2 A | On | [10 empty] | 1,937 ohm | 28 ohm |  | 0 s |  | 2,905 ohm | 32 ohm |  | 0,8 s |  | 28,375 ohm | 35 ohm |  | 1,6 s | [12 empty] | Tap Setting | [46 empty] | Tap Setting | 2000/1A |  | 0,97 A (sec) | 0,44(SI) | - | - |  | 0,16 A (sec) | 0,71(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.36 | GROGOL BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1gJ5AmkFJ6o12Zf8eFWzPGKFDOTg1B8bLkB721FSdClI/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/1A | 150kV/100V |  | 0,016 uF/km | 0,016 uF/km | 0,374 ohm/km | 1,29 / 0,67 | 6,468 km | 82 deg |  | On | 0,2 A (0,2xIn) | 0 | On | 2 A | On | [10 empty] | 1,937 ohm | 28 ohm |  | 0 s |  | 2,905 ohm | 32 ohm |  | 0,8 s |  | 28,375 ohm | 35 ohm |  | 1,6 s | [12 empty] | Tap Setting | [46 empty] | Tap Setting | 2000/1A |  | 0,97 A (sec) | 0,44(SI) | - | - |  | 0,16 A (sec) | 0,71(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.37 | GROGOL BARU | GROGOL | https://docs.google.com/spreadsheets/d/1y_KEthuDmKH7Kmw89cyJGkzUkDYIYRAG2VDfff1zLQ8/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/1A | 150kV/100V |  | 0,016 uF/km | 0,016 uF/km | 0,374 ohm/km | 1,29 / 0,67 | 2 km | 82 deg |  | On | 0,2 A (0,2xIn) | 0 | On | 2 A | On | [10 empty] | 0,599 ohm | 28 ohm |  | 0 s |  | 1,078 ohm | 32 ohm |  | 0,4 s |  | 1,796 ohm | 35 ohm |  | 1,6 s | [12 empty] | Tap Setting | [46 empty] | Tap Setting | 2000/1A |  | 0,97 A (sec) | 0,44(SI) | - | - |  | 0,16 A (sec) | 0,71(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.38 | GROGOL BARU | GROGOL | https://docs.google.com/spreadsheets/d/1-wcH0elM2bE4HU8pItllVy-RmVCos8WejvdoBYK3p3s/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/1A | 150kV/100V |  | 0,016 uF/km | 0,016 uF/km | 0,374 ohm/km | 1,29 / 0,67 | 2 km | 82 deg |  | On | 0,2 A (0,2xIn) | 0 | On | 2 A | On | [10 empty] | 0,599 ohm | 28 ohm |  | 0 s |  | 1,078 ohm | 32 ohm |  | 0,4 s |  | 1,796 ohm | 35 ohm |  | 1,6 s | [12 empty] | Tap Setting | [46 empty] | Tap Setting | 2000/1A |  | 0,97 A (sec) | 0,44(SI) | - | - |  | 0,16 A (sec) | 0,71(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.39 | KEBON JERUK | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1-rDkfQkizAlX0VLdsvC2PMXvj8PPwlCoVvYlYQu2zVQ/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Disabled | - | Enabled | - | - | Enabled | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Tap Setting | 1000/5 A | 150kV/100V | 10,2 km | 0,156 ohm | 72 deg | 0.772 | -17,23 deg |  | 1,5 A | 10 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | - | Disabled | - | Enable PoleDead | 0000011 (Z1 Z2) | Enabled | 0000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,125 ohm | 72 deg | 3,08 ohm | 0,187 ohm | 72 deg | 4,39 ohm | 0,948 ohm | 72 deg | 6,28 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 1000/5 A |  | 4,8 A | 0,49(SI) | - | - |  | 0,8 A | 0,75(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.40 | KEBON JERUK | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1Pbb3-uQViRHekIu8NQJjGnQy3pB8P5rrLUg3yeIKSck/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Disabled | - | Enabled | - | - | Enabled | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Tap Setting | 1000/5 A | 150kV/100V | 10,2 km | 0,16 ohm | 71,57 deg | 0.773 | -17.448 deg |  | 1,5 A | 9.2 A | 30% | 80% | 0 s | - | - | - | - | - | - | [6 empty] | - | - | - | Disabled | - | Disabled | - | Disabled | - | Disabled | - | - |  | Measured + MCB | Disabled | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 1000/5 A |  | 5,52 A | 0,459 SI | - | - |  | 0,92 | 0,739 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.41 | KEBON JERUK | KARET BARU | https://docs.google.com/spreadsheets/d/1iONbCkN9DcoZYBeLDGSiNEIfzUN_qC0vsLU0QL5YHwQ/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 500/5 | 150kV/100V | 5,4 km | - | - | - | - |  | 1,5 A | 10 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  | Measured + MCB | Enabled | - |  | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  | Not Active | - | - | - | - |  | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [14 empty] | Tap Setting | 500/5 |  | 4,3 A | 0,615 SI | - | - |  | 0,725 A | 0,875 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.42 | KEBON JERUK | KARET BARU | https://docs.google.com/spreadsheets/d/106ZFohplNWZhl71Pv_x1VAytkny9X2DfHjhD1ztdd6I/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 500/5 | 150kV/100V | 5,4 km | - | - | - | - |  | 1,5 A | 10 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  | Measured + MCB | Enabled | - |  | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  | Not Active | - | - | - | - |  | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [14 empty] | Tap Setting | 500/5 |  | 4,3 A | 0,615 SI | - | - |  | 0,725 A | 0,875 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.43 | MUARAKARANG BARU | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1_7up2oXNP8bDecvQ03tANwi9DONnbLG1Jq8Hq0k01Mk/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 2000-01-01 | 150/100 | 0.26 km | 0.051 ohm | 72.903 deg | 0.723 | -11.116 deg |  | 0.3 A | 2 A | 30% | 150% | 0 s | Disabled | - | -- | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | Enabled | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000-01-01 |  | 1.2 A | 0.41 SI | Disabled | - |  | 0.2 A | 0.74 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.44 | MUARAKARANG BARU | MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1w8RYbap1AWwu9vGJ7EC6uW-rT5GbJ4Dy_KJDob-KKkU/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 2000-01-01 | 150/100 | 0.22 km | 0.043 ohm | 72.903 deg | 72.3% | -11.116 deg |  | 0.3 A | 2 A | 30% | 150% | 0 s | Disabled | - | -- | - | - | - | [6 empty] | - | - | - | - | - | - | - | - | - | - | - | - |  | - | Enabled | - |  | - | - | - | - | - | - | - | - | - |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000-01-01 |  | 1.2 A | 0.41 SI | Disabled | - |  | 0.2 A | 0.74 SI | Disabled | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.45 | MUARAKARANG BARU | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1Ies8lAx8df_Hsyo3-E-xiirDcgvhD1hz8ZSWqvG-LgI/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 767011 | 150kV/100V | 4.93 km | 15.822 ohm | 81.296 deg | 0.66 | 5.096 deg |  | 0.3 In | 2 In | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0.4 s | 1.6 s | POR | 100 ms | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | I Diff | - |  | 12.657 ohm | 81.296 deg | 29.4 ohm | 22.457 ohm | 81.296 deg | 36.74 ohm | 37.36 ohm | 81.296 deg | 45.93 ohm |  | 1PAR/3PAR | BAR 3ph | 1.5 s | 1 s | 5 s |  | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 767011 |  | 0.754 A | 0.375 SI | - | - |  | 0.126 A | 0.704 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.46 | MUARAKARANG BARU | PANTAI INDAH KAPUK | https://docs.google.com/spreadsheets/d/1lBiXVwY0r9BSraQc-cDQn3CcjxtoQCIDp5xP2nIIfR8/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 767011 | 150kV/100V | 4.93 km | 15.822 ohm | 81.296 deg | 66% | 5.096 deg |  | 0.3 In | 2 In | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0.4 s | 1.6 s | POR | 100 ms | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | I Diff | - |  | 12.657 ohm | 81.296 deg | 29.4 ohm | 22.457 ohm | 81.296 deg | 36.74 ohm | 37.36 ohm | 81.296 deg | 45.93 ohm |  | 1PAR/3PAR | BAR 3ph | 1.5 s | 1 s | 5 s |  | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 767011 |  | 0.754 A | 0.375 SI | - | - |  | 0.126 A | 0.704 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.47 | NEW SENAYAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1lGMff0B0Vx_cn1EmcOhgtwmeHA5UJMtK9UNM2Z8YKhU/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Group 1 | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | -328596 | - | 9.87 km | 0.15 ohm | 72.87 deg | 0.772 | -17.234 deg |  | 0.93 A | 9.25 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | - | - | - | - | - |  | MCB Only | Disabled | Blocking |  | 0,12 ohm | 72,87 deg | 4,38 ohm | 0,18 ohm | 72,87 deg | 4,86 ohm | 0,33 ohm | 72,87 deg | 5,41 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | -328716 |  | 1.11 A | 0.447 SI | Disabled | - |  | 0.185 A | 0.760 SI | Disabled | - | Disabled | Disabled | [17 empty] | Tap Setting Tanggal
PHT.48 | NEW SENAYAN | KEMBANGAN | https://docs.google.com/spreadsheets/d/1uKIjsZbKKW3vINvUVaxo7QdxAKOrLSs1K94710hJecw/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Group 1 | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | -328596 | - | 9.87 km | 0.15 ohm | 72.87 deg | 77.2% | -17.234 deg |  | 0.93 A | 9.25 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | - | - | - | - | - |  | MCB Only | Disabled | Blocking |  | 0,12 ohm | 72,87 deg | 4,38 ohm | 0,18 ohm | 72,87 deg | 4,86 ohm | 0,33 ohm | 72,87 deg | 5,41 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | -328716 |  | 1.11 A | 0.447 SI | Disabled | - |  | 0.185 A | 0.760 SI | Disabled | - | Disabled | Disabled | [17 empty] | Tap Setting Tanggal
PHT.49 | NEW SENAYAN | SENAYAN | https://docs.google.com/spreadsheets/d/1DktR8xxYTa8UgieS5NzFt7Qg96EbC4qfY_5b7-gC73I/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000 / 1 A | 150 kV / 100 V | 5 km | 0.118 ohm | 84 deg | 0.72 | -17.17 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | Disabled |  | Disabled |  |  | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | Disabled |  |  | 0.944 ohm | 84 deg | 33.59 ohm | 1.846 ohm | 84 deg | 41.99 ohm | 3.109 ohm | 84 deg | 52.49 ohm | [7 empty] | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 2000 / 1 A | Group 1 | 0.55 A | 0.47 SI | Disabled | Disabled | Group 1 | 0.1 A | 0.75 SI | Disabled | Disabled | - | - | [17 empty] | Tap Setting Tanggal
PHT.50 | NEW SENAYAN | SENAYAN | https://docs.google.com/spreadsheets/d/15gcmP5VjWWFc3MMiBgZv2QNc3XSUyvcaZkGMF2cYhxI/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000 / 1 A | 150 kV / 100 V | 5 km | 0.118 ohm | 84 deg | 72% | -17.17 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | Disabled |  | Disabled |  |  | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) |  |  | Measured + MCB | Disabled |  |  | 0.944 ohm | 84 deg | 33.59 ohm | 1.846 ohm | 84 deg | 41.99 ohm | 3.109 ohm | 84 deg | 52.49 ohm | [7 empty] | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 2000 / 1 A | Group 1 | 0.55 A | 0.47 SI | Disabled | Disabled | Group 1 | 0.1 A | 0.75 SI | Disabled | Disabled | - | - | [17 empty] | Tap Setting Tanggal
PHT.51 | NEW SENAYAN | ULUJAMI | https://docs.google.com/spreadsheets/d/1MC6UbAz2f9O6ayqUHDH_g7iUjPQQI5-IdXThFVgCHns/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/1 A |  | 0,153 ohm | 0,082 ohm | 0,458 ohm | 0,435 ohm | 0,696 ohm | 0,116 ohm | 3,054 km |  | 0.2 A | 1 | 1 | 0 |  | 0.838 | 0.318 | 61 deg | 0.24 ohm | 0 s | 0.24 ohm | 0 s | 0.433 ohm | 0.4 s | 0.433 ohm | 0.4 s | 0.721 ohm | 1.2 s | 0.721 ohm | 1.2 s | 0.433 ohm | Z1, Z2 and Z3 | POTT |  |  | Enable | Enable | Disable | Disable | Disable | Enable | Disable | Disable | Disable | Not Active | [13 empty] | Tap Setting | 2000-01-01 |  | 0.442 A | 0.45 SI | Disabled | Disabled |  | 0.074 A | 0.747 SI | Disabled | Disabled | - | - | [12 empty] | Tap Setting Tanggal
PHT.52 | NEW SENAYAN | ULUJAMI | https://docs.google.com/spreadsheets/d/1-IJaaTiettplWcaFkecHD5zfnswK8b_tCcnH3d7p_eY/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 2000-01-01 | 150kV/100V | 3.054 km | 0.301 ohm | 61.699 | 0.896 | -20.785 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | POR | 100 ms | Disabled | - | Enable Pole Dead | 000011 | Enable | 000011 |  |  | Measured + MCB | Disabled | Blocking |  | 0.24 ohm | 61.699 deg | 63.45 ohm | 0.433 ohm | 61.699 deg | 70.5 ohm | 1.73 ohm | 61.699 deg | 78.34 ohm |  | Not Active |  |  |  |  | Disabled | [22 empty] | Tap Setting | 2000-01-01 |  | 0.442 A | 0.45 SI | Disabled | Disabled |  | 0.074 A | 0.747 SI | Disabled | Disabled | - | - | [17 empty] | Tap Setting Tanggal
PHT.53 | PANTAI INDAH KAPUK | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1YGa_PVGzABwUO_XdoGaxHbpdee8b9otrhWySIYGOLU0/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V | 4,6 km | 15,312 ohm | 81,3 deg | 0.66 | 5,2 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Blocking | 0 s | Disabled | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 12,249 ohm | 81,338 deg | 28,22 ohm | 18,374 ohm | 81,338 deg | 35,27 ohm | 26,762 ohm | 81,338 deg | 44,09 ohm |  | 1PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 3000/1 A | On | 0,754 A | 0,33 (SI) | - | - | On | 0,126 A | 0,626 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.54 | PANTAI INDAH KAPUK | DAAN MOGOT | https://docs.google.com/spreadsheets/d/13MdaR73iIKtJX5PAgkQ_ZbBPPp-y9QUKpFXvBcltxLw/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V | 4,6 km | 15,312 ohm | 81,3 deg | 0.66 | 5,2 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Blocking | 0 s | Disabled | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 12,249 ohm | 81,338 deg | 28,22 ohm | 18,374 ohm | 81,338 deg | 35,27 ohm | 26,762 ohm | 81,338 deg | 44,09 ohm |  | 1PAR | - | 1,5 s | 1000 ms | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 3000/1 A | On | 0,754 A | 0,33 (SI) | - | - | On | 0,126 A | 0,626 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.55 | PANTAI INDAH KAPUK | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1RkCiSNWQAMb88zA5-RuysCadr4crMJJe0rn_5O97PwU/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 4000/1 A | 150kV/100V | 4,7 km | 15,645 ohm | 81,338 deg | 0.66 | -5,184 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,8 s | 1,6 s |  |  |  |  | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 12,516 ohm | 81,338 deg | 29,4 ohm | 18,774 ohm | 81,338 deg | 36,74 ohm | 19,41 ohm | 81,338 deg | 45,99 ohm |  | Not Active | [5 empty] | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 4000/1 A | On | 0,75 A (sec) | 0,345 (SI) | - | - | On | 0,13 A (sec) | 0,63 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.56 | PANTAI INDAH KAPUK | GIS MUARAKARANG BARU | https://docs.google.com/spreadsheets/d/1bzJMnzBNtFfjomWM7ESw7rkW_8ghzQDOzQFbVksZByg/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 4000/1 A | 150kV/100V | 4,7 km | 15,645 ohm | 81,338 deg | 0.66 | -5,184 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,8 s | 1,6 s |  |  |  |  | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 12,516 ohm | 81,338 deg | 29,4 ohm | 18,774 ohm | 81,338 deg | 36,74 ohm | 19,41 ohm | 81,338 deg | 45,99 ohm |  | Not Active | [5 empty] | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 4000/1 A | On | 0,75 A (sec) | 0,345 (SI) | - | - | On | 0,13 A (sec) | 0,63 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.57 | TOMANG | GROGOL | https://docs.google.com/spreadsheets/d/1HSPLekve4h2FgfFw4r9w23Uh28rpQE0KBO38A1CCU6k/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Disabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,11 km | 0,831 ohm | 85 deg | 0.263 | 26 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,664 ohm | 85 deg | 39 ohm | 1,148 ohm | 85 deg | 43 ohm | 2,38 ohm | 85 deg | 48 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,715 A | 0,4(SI) | - | - | Group 1 | 0,120 A | 0,674(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.58 | TOMANG | GROGOL | https://docs.google.com/spreadsheets/d/1fRlcSaCHamkAJa-kLVTsvRPdIe30kqNbHtcWboAD4Vc/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Disabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,11 km | 0,831 ohm | 85 deg | 0.263 | 26 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,664 ohm | 85 deg | 39 ohm | 1,148 ohm | 85 deg | 43 ohm | 2,38 ohm | 85 deg | 48 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,715 A | 0,4(SI) | - | - | Group 1 | 0,120 A | 0,674(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.59 | ULUJAMI | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1bG5rOiNz_-liuI3ZWq6e9w0Pvo9SQmXx2tLZR0kWhyU/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/1 A |  | 0,153 ohm | 0,082 ohm | 0,458 ohm | 0,435 ohm | 0,696 ohm | 0,116 ohm | 3,054 km |  | 0,2 A | 1 | 1 | 1 |  | 0,838 ohm | 0,318 ohm | 61,699 deg | 0,24 ohm | 0 s | 0,24 ohm | 0 s | 0,982 ohm | 0,4 s | 0,982 ohm | 0,4 s | 5,018 ohm | 1,6 s | 5,018 ohm | 1,6 s | 0,982 ohm | Z1, Z2 and Z3 | PUTT | [25 empty] | Tap Setting | 2000/1 A | Group 1 | 0,442 A | 0,45(SI) | - | - | Group 1 | 0,074 A | 0,747(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.60 | ULUJAMI | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1EHa-YQkKZlA61m19012MYQii-qV-p8Ktr5ULbtaWjp0/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 3,054 km | 0,301 ohm | 61,699 deg | 0.896 | -20,785 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | - | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,24 ohm | 61,699 deg | 63,45 ohm | 0,982 ohm | 61,699 deg | 70,5 ohm | 5,018 ohm | 61,699 deg | 78,34 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,442 A | 0,45(SI) | - | - | Group 1 | 0,074 A | 0,747(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.61 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/18zfpWH0vK84CS9EeyuCUVbranP1Onxw7d50n0ZfT2tU/edit?usp=drive_link | RED670 | Tap Setting | 4000/1 A | 500KV/100V |  | 0,2 Ibase | 1,25 Ibase | 2 Ibase | 30% | 80% | 0,8 Ibase | - | 15% | 30% | On | 0,25 s | - |  | - | - | - | - | - | - | - | - |  | 0 s | 2,139 ohm | 0,188 ohm | 2,139 ohm | 0,188 ohm | 3,714 ohm | 0,573 ohm | 4,492 ohm/loop | 34,094 ohm/loop | 0 s |  | 3,209 ohm | 0,282 ohm | 5,572 ohm | 0,859 ohm | [5 empty] | Tap Setting | 6,738 ohm/loop | 48,706 ohm/loop | 0,4 s |  | 14,682 ohm | 1,299 ohm | 39,201 ohm | 69,58 ohm | 30,832 ohm/loop | 69,58 ohm/loop | 1,6 s |  | On | Off |  | On |  | - | - | - | - | - | - | - | - | - | [5 empty] | On | Forward |  | - | - |  | - | - | - | - |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting | [15 empty] | Tap Setting Tanggal
PHT.62 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1oxan4y0FQIZgplW7ic3vnTaZnOW84GFRmO1fF9bNtgE/edit?usp=drive_link | RED670 | Tap Setting | 4000/1 A | 500KV/100V |  | 0,2 Ibase | 1,25 Ibase | 2 Ibase | 30% | 80% | 0,8 Ibase | - | 15% | 30% | On | 0,25 s | - |  | - | - | - | - | - | - | - | - |  | 0 s | 2,139 ohm | 0,188 ohm | 2,139 ohm | 0,188 ohm | 3,714 ohm | 0,573 ohm | 4,492 ohm/loop | 34,094 ohm/loop | 0 s |  | 3,209 ohm | 0,282 ohm | 5,572 ohm | 0,859 ohm | [5 empty] | Tap Setting | 6,738 ohm/loop | 48,706 ohm/loop | 0,4 s |  | 14,682 ohm | 1,299 ohm | 39,201 ohm | 69,58 ohm | 30,832 ohm/loop | 69,58 ohm/loop | 1,6 s |  | On | Off |  | On |  | - | - | - | - | - | - | - | - | - | [5 empty] | On | Forward |  | - | - |  | - | - | - | - |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting | [15 empty] | Tap Setting Tanggal
PHT.63 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1BfK_HajYZX8ks1L6JFY9oCN2m9qPEcjYXpr9qFUzH6c/edit?usp=drive_link | 7SL87 | Tap Setting | 4000/1 A | 500kV/100V |  | 0,014 uF/km | 0,014 uF/km | 0,191 ohm/km | 0,683/0,245 | 11,188 km | 84,979 deg |  | On | 0,2 A | 0 s | On | 2 A | - |  | On | 10 s |  | Distance Z1,Z2,Z3 |  | - |  | Quad |  | 1,711 ohm | 16,238 ohm | - | 0 s |  | 2,567 ohm | 32,294 ohm | - | 0,4 s |  | 11,746 ohm | 33,289 ohm | - | 1,6 s |  | 1,718 ohm | - | - | 0 s |  | 2,577 ohm | [5 empty] | Tap Setting | - | - |  | 13,635 ohm | - | - | 1,6 s |  | Dist prot | On | 0 s |  | Dist Z1 (QUAD MHO) | Dist Z2 (QUAD MHO) | On | 0,05 s | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.64 | MUARAKARANG BARU | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1-MyjOpotSCGEaWnns23yqX-OV3sWSEvkq5-Q2DE-NcA/edit?usp=drive_link | 7SL87 | Tap Setting | 4000/1 A | 500kV/100V |  | 0,014 uF/km | 0,014 uF/km | 0,191 ohm/km | 0,683/0,245 | 11,188 km | 84,979 deg |  | On | 0,2 A | 0 s | On | 2 A | - |  | On | 10 s |  | Distance Z1,Z2,Z3 |  | - |  | Quad |  | 1,711 ohm | 16,238 ohm | - | 0 s |  | 2,567 ohm | 32,294 ohm | - | 0,4 s |  | 11,746 ohm | 33,289 ohm | - | 1,6 s |  | 1,718 ohm | - | - | 0 s |  | 2,577 ohm | [5 empty] | Tap Setting | - | - |  | 13,635 ohm | - | - | 1,6 s |  | Dist prot | On | 0 s |  | Dist Z1 (QUAD MHO) | Dist Z2 (QUAD MHO) | On | 0,05 s | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.65 | MUARAKARANG BARU | TANJUNG PRIOK |  | RED670 | #N/A
PHT.66 | MUARAKARANG BARU | TANJUNG PRIOK |  | RED670 | #N/A
PHT.67 | MUARAKARANG BARU | TANJUNG PRIOK |  | 7SL87 | #N/A
PHT.68 | MUARAKARANG BARU | TANJUNG PRIOK |  | 7SL87 | #N/A
PHT.69 | CURUG | CIKUPA | https://docs.google.com/spreadsheets/d/1gS4R9JIPm3MxppUtT-afKiselL-PRe9Jkqt5ZeCir5Y/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 18,9 km | 2,261 ohm | 80,731 deg | 0.862 | -31,001 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 1,808 ohm | 80,731 deg | 26,09 ohm | 3,186 ohm | 80,731 deg | 32,62 ohm | 5,986 ohm | 80,731 deg | 40,77 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,85 A | 0,387(SI) | - | - | Group 1 | 0,14 A | 0,663(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.70 | CURUG | CIKUPA | https://docs.google.com/spreadsheets/d/10XThA6g2zUyrvsbjt9c_Yb3G49qXwNzHaO3q8Fs15UI/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3200/1 A | 150kV/100V | 18,6 km | 5,698 ohm | 84,806 deg | 0.75 | -22 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 4,558 ohm | 84,806 deg | 29,56 ohm | 6,837 ohm | 84,806 deg | 36,95 ohm | 14,593 ohm | 84,806 deg | 46,19 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 3200/1 A | Group 1 | 0,531 A | 0,3934(SI) | - | - | Group 1 | 0,0885 A | 0,6755(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.71 | CURUG | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/158xnn4VUt8rYrAHQ9dc9GJtu1bCtB_Xsf08oSfRmVDM/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3200/1 A | 150kV/100V | 4,7 km | 0,903 ohm | 81 deg | 0.861 | -31,18 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,723 ohm | 81 deg | 50,39 ohm | 1,559 ohm | 81 deg | 55,99 ohm | 2,652 ohm | 81 deg | 62,21 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 3200/1 A | Group 1 | 0,542 A | 0,3904(SI) | - | - | Group 1 | 0,091 A | 0,6723(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.72 | CURUG | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/1y0BlikOs-AdK9euUH0YZjzEqA0eL3gT_xEwtq64uPRU/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,7 km | 0,565 ohm | 81 deg | 0.861 | -31,18 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,452 ohm | 81 deg | 31,49 ohm | 0,974 ohm | 81 deg | 34,99 ohm | 1,658 ohm | 81 deg | 38,88 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,87 A | 0,41(SI) | - | - | Group 1 | 0,144 A | 0,685(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.73 | GAJAH TUNGGAL | PASAR KEMIS | https://docs.google.com/spreadsheets/d/15M9aJzZzNu5hlgrMke4A-x8s0Bqc0Sw3YQzyredDJcI/edit?usp=drive_link | L90 | Tap Setting |  | 2000 / 1 A | 150 kV / 100 V |  |  | Disabled | 0.2 pu | 20% | 60% | 1.5 pu | [8 empty] | 1.772 ohm | 82 deg | 90 deg | 45 deg | 90 deg | 34.343 ohm | 79 deg | 34.343 ohm | 79 deg | 0 s |  | 3.425 ohm | 82 deg | 90 deg | 45 deg | 90 deg | 34.343 ohm | 79 deg | 34.343 ohm | 79 deg | 0.4 s | [5 empty] | Tap Setting |  | 5.757 ohm | 82 deg | 90 deg | 45 deg | 90 deg | 34.343 ohm | 79 deg | 34.343 ohm | 79 deg | 1.6 s |  | 1.772 ohm | 75 deg | 90 deg | 45 deg | 60 deg | 34.343 ohm | 79 deg | 34.343 ohm | 79 deg | 0 s |  | 3.425 ohm | 75 deg | 90 deg | 45 deg | 60 deg | 34.343 ohm | 79 deg | 34.343 ohm | 79 deg | 0.4 s |  | 5.757 ohm | 75 deg | 90 deg | 45 deg | 60 deg | 34.343 ohm | 79 deg | 34.343 ohm | 79 deg | 1.6 s | [5 empty] | Tap Setting | Enable | Enable |  | Disable | Disable | Disable |  | Disable | Disable | Disable | Disable | Disable |  | Disable | Disable |  | Disable | Disable | Disable | Disable | Disable |  | Disable | Enable | Disable | Disable | Disable | POTT | [13 empty] | Tap Setting | 2000 / 1 A |  | 0.97 A | 0.337 SI | Disabled | Disabled |  | 0.162 A | 0.586 SI | Disabled | Disabled | [9 empty] | Tap Setting Tanggal
PHT.74 | GAJAH TUNGGAL | PASAR KEMIS BARU | https://docs.google.com/spreadsheets/d/1kC70sE5aQrIpuxGujxYvzZvZXsJUypCKBD4qR5Hbgcc/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 2000 / 1 A | 150 kV / 100 V | 6.6 km | 1.85 ohm | 82 deg | 0.64 | -11 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | [12 empty] | 0 s | 0.4 s | 1.6 s | [14 empty] | 1.48 ohm | 82 deg | 18.7 ohm | 2.326 ohm | 82 deg | 26.71 ohm | 3.807 ohm | 82 deg | 38.16 ohm | [29 empty] | Tap Setting | 2000 / 1 A |  | 0.97 A | 0.34 SI | Disabled | Disabled |  | 0.16 A | 0.61 SI | Disabled | Disabled | [19 empty] | Tap Setting Tanggal
PHT.75 | ITS | TANGERANG BARU | https://docs.google.com/spreadsheets/d/183f3r1m0S_cQEntotSm-DMYWR7td4P67IJDiI6E5k9U/edit?usp=sharing | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 767011 | 150kV/100V | 2.45 km | 4.201 Ohm | 87.3 deg | 0.67 | -3.953 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0s | 0.4s | 1.6s | Disabled | - | Disabled | - | - | - | - | - | - | - | Measured + MCB | Enabled | - |  | 3.361 ohm | 87.3 deg | 25.25 ohm | 10.399 ohm | 87.3 deg | 31.56 ohm | 24.342 ohm | 87.3 deg | 39.46 ohm |  | 1PAR/3PAR | BAR 3ph | - | 1s | 3s |  | 52V | 11.5V | - | V< | Enabled | 15 deg | 6V | 0.167 Hz | [14 empty] | Tap Setting | 767011 |  | 1.124 | 0.212 | - | - |  | 0.187 | 0.473 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.76 | ITS | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1aqNg3Mlr9twgz_hGmVOGxUwz9HbewC6tlkYDjQsfu9g/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 767011 | 150kV/100V | 4.132 km | 6.881 ohm | 87.3 deg | 0.671 | -4.191 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0s | 0.8s | 1.6s | Disabled | - | Disabled | - | - | - | - | - | - | - | Measured + MCB | Enabled | - |  | 5.505 ohm | 87.3 deg | 29.86 ohm | 8.257 ohm | 87.3 deg | 37.32 ohm | 11.692 ohm | 87.3 deg | 46.65 ohm |  | 1PAR/3PAR | BAR 3ph | - | 1s | 3s |  | 52V | 11.5V | - | V< | Enabled | 15 deg | 6V | 0.167 Hz | [14 empty] | Tap Setting | 767011 |  | 0.95 | 0.234 | - | - |  | 0.158 | 0.486 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.77 | ITS | KONSUMEN | https://docs.google.com/spreadsheets/d/1DSkWdSbfURDayk9UcU3AzxdzyZQ16FUv2rJ1ux90TLE/edit?usp=drive_link | 7SL87 | Tap Setting | 300/1 | 150000/100 |  | - | - | - | 0.821/0.667 | 0.08km | 62.709 deg |  | On | 0.2A | 0s | On | 2A | - |  | On | 10s |  | - |  | - |  | - |  | - | - | - | - |  | - | - | - | - |  | - | - | - | - |  | - | - | - | - |  | - | [5 empty] | Tap Setting | - | - |  | - | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 300/1 |  | 1.2 | 0.628 | - | - |  | 0.2 | 0.901 | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.78 | JATAKE | CIKUPA | https://docs.google.com/spreadsheets/d/19rEhayqjtwaWSoT5ZTvIbc5k2NzuDDs1Laia6Fj-Nsc/edit?usp=drive_link | MICOM P442 | Tap Setting | [20 empty] | Tap Setting | [79 empty] | Tap Setting | 2000-05-01 |  | 4.675 A | 0.36 SI | - | - |  | 0.78 A | 0.62 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.79 | JATAKE | CIKUPA | https://docs.google.com/spreadsheets/d/1vzC1yp74fxeW_SkTib1X3vUtPqKeRIPe4QzDFGSWtYE/edit?usp=drive_link | MICOM P442 | Tap Setting | [20 empty] | Tap Setting | [79 empty] | Tap Setting | -109450 |  | 6 A | 0,375 SI | - | - |  | 1 A | 0,635 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.80 | JATAKE | JATAKE BARU | https://docs.google.com/spreadsheets/d/1JeQl8fuBX8efnvZ36FsRC3KOBPdukfNMtC4OZXnd90s/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 1600/5A |  | 0,211 ohm | 0,029 ohm | 0,634 ohm | 0,142 ohm | - | - | 3,53 km |  | 1 | 0,8 *as_site_needed | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 0,171 ohm | 0 s | 0,171 ohm | 0 s | 0,436 ohm | 0,4 s | 0,436 ohm | 0,4 s | 1,111 ohm | 1,2 s | 1,111 ohm | 1,2 s | 0,436 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 1600/5A |  | 6 A | 0,394(SI) | - | - |  | 1 A | 0,66(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.81 | JATAKE | JATAKE BARU | https://docs.google.com/spreadsheets/d/1U4LNFfdRgkG3oTL8LS9vYsoJSOwmdYIxb6iZucimlf8/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 1600/5A |  | 0,211 ohm | 0,029 ohm | 0,634 ohm | 0,142 ohm | - | - | 3,53 km |  | 1 | 0,8 *as_site_needed | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 0,171 ohm | 0 s | 0,171 ohm | 0 s | 0,436 ohm | 0,4 s | 0,436 ohm | 0,4 s | 1,111 ohm | 1,2 s | 1,111 ohm | 1,2 s | 0,436 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 1600/5A |  | 6 A | 0,394(SI) | - | - |  | 1 A | 0,66(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.82 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/15GsUKUcg8JFZFdO28Po0aIH7dQZTMd49pg75AzRjtqc/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 1000/1A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,224 ohm | 1 | 1 | 1 |  | 0.7 | -0.174 | 83,256 deg | [17 empty] | Disable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [13 empty] | Tap Setting | 1000/1A | 50/51P1 | 1,2 A (sec) | 0,405(SI) | - | - | 50/51G4 | 0,2 A (sec) | 0,669(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.83 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1Aq7yTz8ADrd9gs4q9_ofm_8Fmb-bD8-uFGXMHXiPROk/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 1000/1A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,224 ohm | 1 | 1 | 1 |  | 0.7 | -0.174 | 83,256 deg | [17 empty] | Disable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [13 empty] | Tap Setting | 1000/1A | 50/51P1 | 1,2 A (sec) | 0,405(SI) | - | - | 50/51G4 | 0,2 A (sec) | 0,669(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.84 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/15GsUKUcg8JFZFdO28Po0aIH7dQZTMd49pg75AzRjtqc/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 1000/1A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,224 ohm | 1 | 1 | 1 |  | 0.7 | -0.174 | 83,256 deg | [17 empty] | Disable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [13 empty] | Tap Setting | 1000/1A | 50/51P1 | 1,2 A (sec) | 0,405(SI) | - | - | 50/51G4 | 0,2 A (sec) | 0,669(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.85 | JATAKE | MAXIMANGANDO | https://docs.google.com/spreadsheets/d/1Aq7yTz8ADrd9gs4q9_ofm_8Fmb-bD8-uFGXMHXiPROk/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 1000/1A |  | 0,075 ohm | 0,009 ohm | 0,224 ohm | 0,066 ohm | - | - | 0,99 km |  | 0,224 ohm | 1 | 1 | 1 |  | 0.7 | -0.174 | 83,256 deg | [17 empty] | Disable |  |  |  | Disable | Enable | Enable |  | Disable | Not Active | [13 empty] | Tap Setting | 1000/1A | 50/51P1 | 1,2 A (sec) | 0,405(SI) | - | - | 50/51G4 | 0,2 A (sec) | 0,669(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.86 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/11n1GJXlqbL-fua2lnF0pUvVF-UHI58wZnqL0wpwUnJE/edit?usp=drive_link | PCS-931 | Tap Setting | 150 kV / 100 V | 1000 / 1 A |  | 0.075 ohm | 0.009 ohm | 0.224 ohm | 0.066 ohm | - | - | 0.99 km |  | 0.2 A | 1 | 1 | - |  | 0.7 | 0.174 | 83.256 deg | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [13 empty] | Tap Setting | 1000 / 1 A |  | 1,2 A (sec) | 0,402 SI | - | - |  | 0,2 A (sec) | 0,665 SI | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.87 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/1Y0-J-8ad6pziDYgoE37bzaxqgoc9kqSEsFjNgaD3L7A/edit?usp=drive_link | PCS-931 | Tap Setting | 150 kV / 100 V | 1000 / 1 A |  | 0.075 ohm | 0.009 ohm | 0.224 ohm | 0.066 ohm | - | - | 0.99 km |  | 0.2 A | 1 | 1 | - |  | 70% | 0.174 | 83.256 deg | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [13 empty] | Tap Setting | 1000 / 1 A |  | 1,2 A (sec) | 0,402 SI | - | - |  | 0,2 A (sec) | 0,665 SI | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.88 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/11n1GJXlqbL-fua2lnF0pUvVF-UHI58wZnqL0wpwUnJE/edit?usp=drive_link | PCS-931 | Tap Setting | 150 kV / 100 V | 1000 / 1 A |  | 0.075 ohm | 0.009 ohm | 0.224 ohm | 0.066 ohm | - | - | 0.99 km |  | 0.2 A | 1 | 1 | - |  | 0.7 | 0.174 | 83.256 deg | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [13 empty] | Tap Setting | 1000 / 1 A |  | 1,2 A (sec) | 0,402 SI | - | - |  | 0,2 A (sec) | 0,665 SI | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.89 | MAXIMANGANDO | JATAKE | https://docs.google.com/spreadsheets/d/1Y0-J-8ad6pziDYgoE37bzaxqgoc9kqSEsFjNgaD3L7A/edit?usp=drive_link | PCS-931 | Tap Setting | 150 kV / 100 V | 1000 / 1 A |  | 0.075 ohm | 0.009 ohm | 0.224 ohm | 0.066 ohm | - | - | 0.99 km |  | 0.2 A | 1 | 1 | - |  | 70% | 0.174 | 83.256 deg | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled |  |  |  | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Disable | Not Active | [13 empty] | Tap Setting | 1000 / 1 A |  | 1,2 A (sec) | 0,402 SI | - | - |  | 0,2 A (sec) | 0,665 SI | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.90 | SINDANG JAYA | BALARAJA | https://docs.google.com/spreadsheets/d/1IK2DYZcHm5MkukKyo1x7sG4osnO77byJ3aebcjgBbsQ/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 4000/1A |  | 3,339 ohm | 0,426 ohm | 10,016 ohm | 2,202 ohm | - | - | 7,69 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 82,275 deg | 4,664 ohm | 0 s | 4,664 ohm | 0 s | 7,956 ohm | 0,4 s | 7,956 ohm | 0,4 s | 17,278 ohm | 1,6 s | 17,278 ohm | 1,6 s | 19,917 ohm | Z2 and Z3 | POTT |  | Disable | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) | - | - | 50/51G4 | 0,137 A (sec) | 0,625(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.91 | SINDANG JAYA | BALARAJA | https://docs.google.com/spreadsheets/d/15gdVi4iRgc364cz2LCPXPoymgaYb-bXkYVqk5pMWfhs/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 4000/1A |  | 3,339 ohm | 0,426 ohm | 10,016 ohm | 2,202 ohm | - | - | 7,69 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 82,275 deg | 4,664 ohm | 0 s | 4,664 ohm | 0 s | 7,956 ohm | 0,4 s | 7,956 ohm | 0,4 s | 17,278 ohm | 1,6 s | 17,278 ohm | 1,6 s | 19,917 ohm | Z2 and Z3 | POTT |  | Disable | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) | - | - | 50/51G4 | 0,137 A (sec) | 0,625(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.92 | SINDANG JAYA | LONTAR | https://docs.google.com/spreadsheets/d/1U-e69FkdoUL2MHWdFa_2hYYwWbYENik7Czn_T0sXlm8/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 4000/1A |  | 9,36 ohm | 1,275 ohm | 28,079 ohm | 6,307 ohm | 9,937 ohm | 1,654 ohm | 12,58 km | [6 empty] | 0.68 | - 0,087 ohm | 82,24 deg | 7,557 ohm | 0 s | 7,557 ohm | 0 s | 19,917 ohm | 0,4 s | 19,917 ohm | 0,4 s | 37,368 ohm | 1,6 s | 37,368 ohm | 1,6 s | 19,917 ohm | Z2 and Z3 | PUTT |  | Disable | Enable |  | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 4000/1A | 50/51P3 | 0,82 A (sec) | 0,374(SI) | - | - | 50/51G3 | 0,137 A (sec) | 0,65(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.93 | SINDANG JAYA | LONTAR | https://docs.google.com/spreadsheets/d/1qwiSHMFlcv5bowRY0YFSepceEHpXtH9gAImbRim5Et4/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 4000/1A |  | 9,36 ohm | 1,275 ohm | 28,079 ohm | 6,307 ohm | 9,937 ohm | 1,654 ohm | 12,58 km | [6 empty] | 0.68 | - 0,087 ohm | 82,24 deg | 7,557 ohm | 0 s | 7,557 ohm | 0 s | 19,917 ohm | 0,4 s | 19,917 ohm | 0,4 s | 37,368 ohm | 1,6 s | 37,368 ohm | 1,6 s | 19,917 ohm | Z2 and Z3 | PUTT |  | Disable | Enable |  | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 4000/1A | 50/51P3 | 0,82 A (sec) | 0,374(SI) | - | - | 50/51G3 | 0,137 A (sec) | 0,65(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.94 | SINDANG JAYA | SUVARNA SUTERA | https://docs.google.com/spreadsheets/d/1O4iMK9fq5D-Ra0BlxdvdxrAQVSVgmVroY1RpVxIVvxk/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 4000/1A |  | 1,98 ohm | 0,253 ohm | 5,939 ohm | 1,306 ohm | - | - | 4,56 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 82,725 deg | 2,776 ohm | 0 s | 2,776 ohm | 0 s | 5,628 ohm | 0,4 s | 5,628 ohm | 0,4 s | 9,516 ohm | 1,2 s | 9,516 ohm | 1,2 s |  | Z2 and Z3 | POTT |  | Disable | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) | - | - | 50/51G4 | 0,137 A (sec) | 0,625(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.95 | SINDANG JAYA | SUVARNA SUTERA | https://docs.google.com/spreadsheets/d/1zgS9FZQl2jleL4mQE63ZxZbLXZjVl3s33lWSd_btP9I/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 4000/1A |  | 1,98 ohm | 0,253 ohm | 5,939 ohm | 1,306 ohm | - | - | 4,56 km |  | 0,2 A | 1 A | 1 | 1 |  | 0.68 | -0.091 | 82,725 deg | 2,776 ohm | 0 s | 2,776 ohm | 0 s | 5,628 ohm | 0,4 s | 5,628 ohm | 0,4 s | 9,516 ohm | 1,2 s | 9,516 ohm | 1,2 s |  | Z2 and Z3 | POTT |  | Disable | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 4000/1A | 50/51P4 | 0,819 A (sec) | 0,359(SI) | - | - | 50/51G4 | 0,137 A (sec) | 0,625(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.96 | TANGERANG BARU | LONTAR | https://docs.google.com/spreadsheets/d/1DThmS_TVshKSUqPXvHlRCDS8SSllAv9njZSdiiIxYzA/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3000/1 A | 150kV/100V | 21,23 km | 11,284 ohm | 76,22 deg | 0.674 | -2,423 deg |  | 0,2 xIn | 2 xIn | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | I Diff + standart | - |  | 9,027 ohm | 76,22 deg | 35,32 ohm | 14,142 ohm | 76,22 deg | 39,25 ohm | 21,532 ohm | 76,22 deg | 49,06 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.97 | TANGERANG BARU | LONTAR | https://docs.google.com/spreadsheets/d/1XrLp-G8k7jH4zGHSxyHG0NR2ILCmpE7qbBrtiIPAO50/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3000/1 A | 150kV/100V | 21,23 km | 11,284 ohm | 76,22 deg | 0.674 | -2,423 deg |  | 0,2 xIn | 2 xIn | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | I Diff + standart | - |  | 9,027 ohm | 76,22 deg | 35,32 ohm | 14,142 ohm | 76,22 deg | 39,25 ohm | 21,532 ohm | 76,22 deg | 49,06 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.98 | TANGERANG BARU | ITS | https://docs.google.com/spreadsheets/d/1it9FF1xe83IbwSASHWr6oaErJsEriRUqQaS56v-8wJI/edit?usp=sharing | MICOM P545 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | 401769 |  | 1.2 A | 0.222 SI | - | - |  | 0.2 A | 0.469 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.99 | TANGERANG BARU | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1j9UPZUhHwjANqFfmzKGm3xEdGXc1O7eyNWCa34mR_Ho/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/1 A | 150kV/100V | 6,3 km | 10,804 km | 87,293 deg | 0.67 | -3,953 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 (Z2 Z3) | - |  | Measured + MCB | Disabled | - |  | 8,643 ohm | 87,293 deg | 29,69 ohm | 15,13 ohm | 87,293 deg | 32,99 ohm | 28,221 ohm | 87,293 deg | 36,66 ohm |  | 1PAR/3PAR | BAR 2 and 3 ph | 500 ms | 1 s | 3 s |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 0,17 Hz | [14 empty] | Tap Setting | 401769 |  | 1,2 A | 0,222 (SI) | - | - |  | 0,2 A | 0,469 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.100 | TELUK NAGA | DADAP | https://docs.google.com/spreadsheets/d/1YIxxO10MIvc8tyb1gtdpGEiZdlhWW1RuxusmJ2kgMWk/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 3000 /1 A | 150 kV / 100 V | 6.132 km | 3.487 ohm | 82.725 deg | 0.684 | -7.618 |  | 0.2 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | - | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 |  |  | Measured + MCB | Disabled | - |  | 2.789 ohm | 82.725 deg | 25.7 ohm | 12.1 ohm | 82.725 deg | 28.55 ohm | 21.642 ohm | 82.725 deg | 31.72 ohm | [7 empty] | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 3000 / 1 |  | 1.092 A | 0.269 SI | - | - |  | 0.182 A | 0.531 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.101 | TELUK NAGA | DADAP | https://docs.google.com/spreadsheets/d/1z7IEr0_A4Qi-QOKuYJdiDxj_6tXWqtlKbaN-WPlrQSc/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 3000 /1 A | 150 kV / 100 V | 6.132 km | 3.487 ohm | 82.725 deg | 0.68 | -7.618 deg |  | 0.2 A | 2 A | 30% | 150% | 0 s | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | [6 empty] | 0 s | 0.4 s | 1.6 s | PUR | - | Disabled | - | Enabled PoleDead | 000011 | Enabled | 000011 |  |  | Measured + MCB | Disabled | - |  | 2.789 ohm | 82.725 deg | 25.7 ohm | 12.1 ohm | 82.725 deg | 28.55 ohm | 21.642 ohm | 82.725 deg | 31.72 ohm | [7 empty] | 52 V | 11.5 V | Enabled | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 3000 / 1 |  | 1.092 A | 0.269 SI | - | - |  | 0.182 A | 0.531 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.102 | TELUK NAGA | SEPATAN | https://docs.google.com/spreadsheets/d/1ktTfifoI-vKO265I_tJpjGjERcLVVWM0vTqYn7dHHz0/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | -109571 | 150kV/100V | 9,17 km | 2,77 ohm | 82,15 deg | 0.685 | -7.244 deg |  | 0,2 A | 2 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,8 s | 1,2 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 2,22 ohm | 82,15 deg | 20,25 ohm | 3,32 ohm | 82,15 deg | 22,5 ohm | 4,52 ohm | 82,15 deg | 25 ohm |  | 1PAR/3PAR | BAR 3 Phase | 0,9 s | 1 | 3 |  | 31,75 V | 11,55 V | Enabled | V< V> and Vdiff> | Enabled | 15 deg | 5,77 V | 0,17 Hz | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.103 | TELUK NAGA | SEPATAN | https://docs.google.com/spreadsheets/d/1yDYsqFIpydB6CDBSYEp9OYWIaUX7Qsm0ROMrl7QLxuE/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | -109571 | 150kV/100V | 9,17 km | 2,77 ohm | 82,15 deg | 0.685 | -7.244 deg |  | 0,2 A | 2 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,8 s | 1,2 s | PUR | 0,1 s | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 2,22 ohm | 82,15 deg | 20,25 ohm | 3,32 ohm | 82,15 deg | 22,5 ohm | 4,52 ohm | 82,15 deg | 25 ohm |  | 1PAR/3PAR | BAR 3 Phase | 0,9 s | 1 | 3 |  | 31,75 V | 11,55 V | Enabled | V< V> and Vdiff> | Enabled | 15 deg | 5,77 V | 0,17 Hz | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.104 | JATAKE BARU | JATAKE | https://docs.google.com/spreadsheets/d/13ZV4tc5EeW_qFPs7NnfQ2SjrrN8e_QqBhLSaJPdzk6g/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/1A |  | 1,321 ohm | 0,182 ohm | 3,963 ohm | 0,888 ohm | - | - | 3,53 km |  | 0,2 A | 1 *as_site_needed | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 1,067 ohm | 0 s | 1,067 ohm | 0 s | 1,6 ohm | 0,8 s | 1,6 ohm | 0,8 s | 4,874 ohm | 1,2 s | 4,874 ohm | 1,2 s | 1,6 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000/1A | 50/51P1 | 0,972 A (sec) | 0,374(SI) | - | - | 50/51G4 | 0,162 A (sec) | 0,636(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.105 | JATAKE BARU | JATAKE | https://docs.google.com/spreadsheets/d/1lBAwbE9vWR6-QkBtTryO638VTZndtaM_wGX5y9820pQ/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/1A |  | 1,321 ohm | 0,182 ohm | 3,963 ohm | 0,888 ohm | - | - | 3,53 km |  | 0,2 A | 1 *as_site_needed | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 1,067 ohm | 0 s | 1,067 ohm | 0 s | 1,6 ohm | 0,8 s | 1,6 ohm | 0,8 s | 4,874 ohm | 1,2 s | 4,874 ohm | 1,2 s | 1,6 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000/1A | 50/51P1 | 0,972 A (sec) | 0,374(SI) | - | - | 50/51G4 | 0,162 A (sec) | 0,636(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.106 | JATAKE BARU | TANGERANG | https://docs.google.com/spreadsheets/d/1HFvkvO46ebK0mXTuH1HXRgQR220W2IwVUMjfwdwWwC0/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/1A |  | 2,571 ohm | 0,354 ohm | 7,714 ohm | 1,728 ohm | - | - | 6,87 km |  | 0,2 A | 1 *as_site_needed | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 2,076 ohm | 0 s | 2,076 ohm | 0 s | 7,348 ohm | 0,4 s | 7,348 ohm | 0,4 s | 12,998 ohm | 1,6 s | 12,998 ohm | 1,6 s | 7,348 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000/1A | 50/51P1 | 0,972 A (sec) | 0,374(SI) | - | - | 50/51G4 | 0,162 A (sec) | 0,636(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.107 | JATAKE BARU | TANGERANG | https://docs.google.com/spreadsheets/d/1c5pCIMYCr_m4Ih5QsIqFUlh0E-R6Xkney5ZWW5CibeA/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/1A |  | 2,571 ohm | 0,354 ohm | 7,714 ohm | 1,728 ohm | - | - | 6,87 km |  | 0,2 A | 1 *as_site_needed | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 2,076 ohm | 0 s | 2,076 ohm | 0 s | 7,348 ohm | 0,4 s | 7,348 ohm | 0,4 s | 12,998 ohm | 1,6 s | 12,998 ohm | 1,6 s | 7,348 ohm | Z2 and Z3 | POTT |  |  | Enable |  |  |  | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000/1A | 50/51P1 | 0,972 A (sec) | 0,374(SI) | - | - | 50/51G4 | 0,162 A (sec) | 0,636(SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.108 | LONTAR | SINDANG JAYA | https://docs.google.com/spreadsheets/d/1Mad--6xOYKdlWz7byYqWgJJ2U-IDHngdf14uvAKoHyk/edit?usp=drive_link | MICOM P443 | Tap Setting |  | Enabled | Enabled | Disabled | N/A | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 4000/1A | 150kV/100V |  | 12.58 km | 9.446 ohm | 82.2 deg | 0.68 | -7.29 deg | 7.557 ohm | 23.212 ohm | - | 0 s | 11.335 ohm | 33.161 ohm | - | 0.4 s | 18.331 ohm | 47.372 ohm | - | [7 empty] | PUR/PUP Z2 | 0 s |  |  | Enabled Pole Dead | 30 s | Disabled | Blocking |  |  |  |  | Measured + MCB | Enabled |  | Not Active | [7 empty] | 11.5 V | 52 V | 11.5 V | 52 V | 6 V | 0.167 Hz | 15 deg | [23 empty] | Tap Setting | 4000/1 A | Group 1 | 0.82 A | 0.346 SI | - | - | Group 1 | 0.137 A | 0.642 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.109 | LONTAR | SINDANG JAYA | https://docs.google.com/spreadsheets/d/1r7qBDETtEcGGFVwKJvmQXfFoCOcMy-x_xN0dXZsT5MY/edit?usp=drive_link | MICOM P443 | Tap Setting |  | Enabled | Enabled | Disabled | N/A | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 4000/1A | 150kV/100V |  | 12.58 km | 9.446 ohm | 82.2 deg | 0.68 | -7.29 deg | 7.557 ohm | 23.212 ohm | - | 0 s | 11.335 ohm | 33.161 ohm | - | 0.4 s | 18.331 ohm | 47.372 ohm | - | [7 empty] | PUR/PUP Z2 | 0 s |  |  | Enabled Pole Dead | 30 s | Disabled | Blocking |  |  |  |  | Measured + MCB | Enabled |  | Not Active | [7 empty] | 11.5 V | 52 V | 11.5 V | 52 V | 6 V | 0.167 Hz | 15 deg | [23 empty] | Tap Setting | 4000/1 A | Group 1 | 0.82 A | 0.346 SI | - | - | Group 1 | 0.137 A | 0.642 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.110 | LONTAR | DADAP | https://docs.google.com/spreadsheets/d/1_n9Zp7Y2NoT_qqHqUVK3QLyxdX4QlC3zjlX8DHlFcy0/edit?usp=drive_link | MICOM P446 | Tap Setting |  | Enabled | Enabled | Disabled |  | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 3000 / 1 A | 150 kV / 100 V |  | 25.588 km | 14.549 ohm | 82.725 deg | 0.684 | -7.618 deg | 11.639 ohm | 82.725 deg | 25.70 ohm | 0 s | 17.459 ohm | 28.55 ohm | 28.55 ohm | 0.4 s | 21.642 ohm | 31.72 ohm | 31.72 ohm | [6 empty] | - | PUR | 0 s | - | - | Enabled PoleDead | 30 s | Disabled | - | - | - | - |  | Measured + MCB | Disabled |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | - | [23 empty] | Tap Setting | 401769 |  | 1.092 | 0.304 | - | - |  | 0.182 | 0.617 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.111 | LONTAR | DADAP | https://docs.google.com/spreadsheets/d/16N_hQUDTAm-C31zmw9FvHAx4H116toI10NQHsNfMECA/edit?usp=drive_link | MICOM P446 | Tap Setting |  | Enabled | Enabled | Disabled |  | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 3000 / 1 A | 150 kV / 100 V |  | 25.588 km | 14.549 ohm | 82.725 deg | 68.4% | -7.618 deg | 11.639 ohm | 82.725 deg | 25.70 ohm | 0 s | 17.459 ohm | 28.55 ohm | 28.55 ohm | 0.4 s | 21.642 ohm | 31.72 ohm | 31.72 ohm | [6 empty] | - | PUR | 0 s | - | - | Enabled PoleDead | 30 s | Disabled | - | - | - | - |  | Measured + MCB | Disabled |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | - | [23 empty] | Tap Setting | 401769 |  | 1.092 | 0.304 | - | - |  | 0.182 | 0.617 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.112 | LONTAR | TANGERANG BARU | https://docs.google.com/spreadsheets/d/1GK01xt7hoqWLkwpSKVVMm3hH1gWFgjsGNpxPWiTE3es/edit?usp=drive_link | MICOM P546 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | CT: 401769; I>: 1.059; tms: 0.362; I>: 0.177; tms: 0.677 | [19 empty] | Tap Setting Tanggal
PHT.113 | LONTAR | TANGERANG BARU | https://docs.google.com/spreadsheets/d/16vozHIoxHVT0qgs6hajKPjl1Z7aNoJy71doFQVnw1co/edit?usp=drive_link | MICOM P546 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | 401769 |  | 109% | 33% | - | - |  | 0.18 | 0.63 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.114 | CENGKARENG | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1Ww0Df6e_JdVjjcwy_b2eezckHonTWQ-IdRlbOe5HyMI/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 2000/5 A | 150kV/100V | 10,32 km | 1,272 ohm | 84,339 deg | 0.672 | -3,623 deg |  | 1 A (0,2xIn) | 10 A (2xIn) | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,8 s | 1,6 s | PUR | 100 ms | Disabled | - | Enable PoleDead | 000110 (Z1 Z2) | Enabled | 000110 (Z1 Z2) | - |  | Measured + MCB | I Diff | - |  | 1,018 ohm | 84,339 deg | 5,81 ohm | 1,527 ohm | 84,339 deg | 6,45 ohm | 2,699 ohm | 84,339 deg | 7,17 ohm |  | 1PAR/3PAR | BAR 3 Phase | 100 ms | 1 s | 3 s |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/5 A | Group 1 | 4,8 A (sec) | 0,34(SI) | - | - | Group 1 | 0,8 A (sec) | 0,59(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.115 | CENGKARENG | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1QUT6oi3kKdCYExcT1xM-NcNSsZ0oFRc9vPIlOoAwGZA/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | Enabled | - | - | - | - | Enabled | - | - | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 2000/5 A | 150kV/100V | 10,32 km | 1,272 ohm | 84,339 deg | 0.672 | -3,623 deg |  | 0,2xIn (1A) | 2xIn (10A) | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,8 s | 1,6 s | PUR | 100 ms | Disabled | - | Enable PoleDead | 000110 (Z1 Z2) | Enabled | 000110 (Z1 Z2) | - |  | Measured + MCB | I Diff | - |  | 1,018 ohm | 84,339 deg | 5,81 ohm | 1,527 ohm | 84,339 deg | 6,45 ohm | 2,699 ohm | 84,339 deg | 7,17 ohm |  | 1PAR/3PAR | BAR 3 Phase | 100 ms | 1 s | 3 s |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/5 A | Group 1 | 4,8 A (sec) | 0,34(SI) | - | - | Group 1 | 0,8 A (sec) | 0,59(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.116 | CENGKARENG | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/13dqZROd78XDCm2sGvj4Xk-DGTIpsIokV60v4XNI-RxI/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3000/5 A | 150kV/100V | 0,397 km | 0,05 ohm | 88,797 deg | 0.686 | -12,314 deg |  | 1 A (0,2xIn) | 10 A (2xIn) | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | - | 88,797 deg | 4,43 ohm | 0,315 ohm | 88,797 deg | 5,54 ohm | 2,329 ohm | 88,797 deg | 6,93 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 3000/5 A | Group 1 | 6 A (sec); (1,2xIn) | 0,242(SI) | - | - | Group 1 | 1 A (sec); (0,2xIn) | 0,496(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.117 | CENGKARENG | CENGKARENG BARU | https://docs.google.com/spreadsheets/d/1JZKV5Er1VvbzG3V4qGwYW__IxmqcaY9PcJlYJ3nx0dU/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3000/5 A | 150kV/100V | 0,397 km | 0,05 ohm | 88,797 deg | 0.686 | -12,314 deg |  | 1 A (0,2xIn) | 10 A (2xIn) | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | - | 88,797 deg | 4,43 ohm | 0,315 ohm | 88,797 deg | 5,54 ohm | 2,329 ohm | 88,797 deg | 6,93 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 3000/5 A | Group 1 | 6 A (sec); (1,2xIn) | 0,242(SI) | - | - | Group 1 | 1 A (sec); (0,2xIn) | 0,496(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.118 | CENGKARENG | TANGERANG | https://docs.google.com/spreadsheets/d/1hMhfYciYCyp6nppuMwlWI0AgiOB2ycLbQyc1toMrvVA/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/5 A | 150kV/100V |  | *)Calculation Note | *)Calculation Note | 0,06 ohm/km | 1,29 / 0,667 | 9,23 km | 82 deg |  | On | 0,2In | 0 | On | 2In | On |  | On | 10 s |  | - |  | - |  | - |  | 0,949 ohm | 5,502 ohm | - | 0 s |  | 1,424 ohm | 10,881 ohm | - | 0,4 s |  | 2,041 ohm | 10,994 ohm | - | 1,6 s |  | 0,96 ohm | - | - | 0 s |  | 1,44 ohm | [5 empty] | Tap Setting | - | - |  | 2,063 ohm | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 2000/5 A |  | 3,75 A | 0.373 SI | - | - |  | 0,625 A | 0.632 SI | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.119 | CENGKARENG | TANGERANG | https://docs.google.com/spreadsheets/d/18jqihAmmeb2YC5TZsLMIy1aWMYLf-AeSuu5MZ9oHZ_Q/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/5 A | 150kV/100V |  | *)Calculation Note | *)Calculation Note | 0,06 ohm/km | 1,29 / 0,667 | 9,23 km | 82 deg |  | On | 0,2In | 0 | On | 2In | On |  | On | 10 s |  | - |  | - |  | - |  | 0,949 ohm | 5,502 ohm | - | 0 s |  | 1,424 ohm | 10,881 ohm | - | 0,4 s |  | 2,041 ohm | 10,994 ohm | - | 1,6 s |  | 0,96 ohm | - | - | 0 s |  | 1,44 ohm | [5 empty] | Tap Setting | - | - |  | 2,063 ohm | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 2000/5 A |  | 3,75 A | 0,373 SI | - | - |  | 0,625 A | 0,632 SI | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.120 | CENGKARENG BARU | BANDARA SOEKARNO HATTA | https://docs.google.com/spreadsheets/d/1EkKq7YMaHRlfUW5Swjcx_w5QxNJkVmtLd-tOb3UCuwk/edit?usp=drive_link | 7SL87 | Tap Setting | 1000/1A | 150kV/100V | [8 empty] | ON | 0,2 A | 0 s | ON | 2 A | ON | [36 empty] | Tap Setting | [46 empty] | Tap Setting | 1000/1A |  | 0,886 A | 0,427(SI) | - | - |  | 0,148 A | 0,686(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.121 | CENGKARENG BARU | BANDARA SOEKARNO HATTA | https://docs.google.com/spreadsheets/d/1OvlR6HmEdqGju8L5nGM4xZtiFr_YodYcBzsyiLyxnuw/edit?usp=drive_link | 7SL87 | Tap Setting | 1000/1A | 150kV/100V | [8 empty] | ON | 0,2 A | 0 s | ON | 2 A | ON | [36 empty] | Tap Setting | [46 empty] | Tap Setting | 1000/1A |  | 0,886 A | 0,427(SI) | - | - |  | 0,148 A | 0,686(SI) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.122 | CENGKARENG BARU | CENGKARENG | https://docs.google.com/spreadsheets/d/1HXicHZIQ-GaHmPJoF8vtEUceUxVAoEQiqCSAlFHGUrA/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 4000/1 A | 150kV/100V | 0,397 km | 0,33 ohm | 88,797 deg | 0.686 | -12,314 deg |  | 1A | 10A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,264 ohm | 88,797 deg | 27,99 ohm | 7,944 ohm | 88,797 deg | 34,99 ohm | 15,661 ohm | 88,797 deg | 43,74 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 4000/1 A |  | 0,945 A | 0,235(SI) | - | - |  | 0,158 A | 0,487(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.123 | CENGKARENG BARU | CENGKARENG | https://docs.google.com/spreadsheets/d/1yfy5JZXISpMVw-R3sugttS_dRI-Hx6azWvD1B-sZDCI/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 4000/1 A | 150kV/100V | 0,397 km | 0,33 ohm | 88,797 deg | 0.686 | -12,314 deg |  | 1A | 10A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,264 ohm | 88,797 deg | 27,99 ohm | 7,944 ohm | 88,797 deg | 34,99 ohm | 15,661 ohm | 88,797 deg | 43,74 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 4000/1 A |  | 0,945 A | 0,235(SI) | - | - |  | 0,158 A | 0,487(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.124 | CENGKARENG BARU | ITS | https://docs.google.com/spreadsheets/d/1TON7JqybXDQqv5vep4Ymt07iau7ilPQK1o_I-t6yI8o/edit?usp=drive_link | MICOM P545 | Tap Setting | [20 empty] | Tap Setting | [80 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.125 | CENGKARENG BARU | TANGERANG BARU | https://docs.google.com/spreadsheets/d/187-jnRs8IP1RBfMsN8Deaa19nu7R9MTbl6LW4Way4Lk/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Enabled |  | Tap Setting | 4000/5 A | 150kV/100V | 6,3 km | 2,161 ohm | 87,293 deg | 0.67 | -3,953 deg |  | 1A | 10A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Enabled | - |  | 1,729 ohm | 87,293 deg | 5,94 ohm | 3,786 ohm | 87,293 deg | 6,6 ohm | 6,451 ohm | 87,293 deg | 7,33 ohm |  | 1PAR/3PAR |  | 500 ms | 1 s | 3 s |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 4000/1 A |  | 1,14 A | 0,137 (SI) | - | - |  | 0,19 A | 0,371 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.126 | CILEDUG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/1qN3MTSsZnLG3qoJeJFPXVcBHA3Dub-C1AzliJvcwRiw/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3000/1A | 150kV/100V | 3,25 km | 0,417 ohm | 76,971 deg | 1.015 | -37,193 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enabled PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,333 ohm | 76,971 deg | 38,81 ohm | 1,117 ohm | 76,971 deg | 48,52 ohm | 1,969 ohm | 76,971 deg | 60,65 ohm |  | Not Active | - | - | - | - |  | 52V | 12V | - | V< | Enabled | 15 deg | 6V | 170 mHz | [14 empty] | Tap Setting | 3000/1A | Group 1 | 0,57 A | 0,415(SI) | - | - | Group 1 | 0,095 A | 0,715(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.127 | CILEDUG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/1y_xOr_sxzk3LIPrpPEqdRzcuSHy-FasJkN1wOD-g8M0/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1A | 150kV/100V | 3,25 km | 0,278 ohm | 76,971 deg | 1.015 | -37,193 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | - | - | - | - | Enabled PoleDeada | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,222 ohm | 76,971 deg | 25,88 ohm | 0,745 ohm | 76,971 deg | 32,34 ohm | 1,313 ohm | 76,971 deg | 40,43 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 2000/1A | Group 1 | 0,86 A | 0,415(SI) | - | - | Group 1 | 0,145 A | 0,71(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.128 | CILEDUG | METLAND | https://docs.google.com/spreadsheets/d/1ju8zrULuJkIKPGtaIk07pjwv4dk_2KLfGRBcCPJn5H0/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 3200/1A | 150kV/100V | 5,356 km | 6,905 ohm | 77,091 deg | 0.655 | 5,653 deg |  | 0,3xIn | 2xIn | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | POR | 100 ms | Disabled | - | Enabled PoleDead | 000011(Z1 Z2) | Enabled | 000011(Z1 Z2) | - |  | Measured + MCB | I Diff | - |  | 5,524 ohm | 77,091 deg | 42,9 ohm | 8,285 ohm | 77,091 deg | 53,63 ohm | 11,774 ohm | 77,091 deg | 67,04 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 3200/1A | Group 1 | 0,517 A (sec) | 0,42(SI) | - | - | Group 1 | 0,086 A (sec) | 0,718(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.129 | CILEDUG | METLAND | https://docs.google.com/spreadsheets/d/1iSOMAut5iinyns6FiHrDFv6I9zmGMSbvnura3yLC7Aw/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1A | 150kV/100V | 5,356 km | 4,315 ohm | 77,091 deg | 0.655 | 5,653 deg |  | 0,3xIn | 2xIn | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | POR | 100 ms | Disabled | - | Enabled PoleDead | 000011(Z1 Z2) | Enabled | 000011(Z1 Z2) | - |  | Measured + MCB | I Diff | - |  | 3,452 ohm | 77,091 deg | 26,81 ohm | 5,178 ohm | 77,091 deg | 33,52 ohm | 7,359 ohm | 77,091 deg | 41,9 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/1A | Group 1 | 0.827 | 0.42SI | - | - | Group 1 | 0.138 | 0.718SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.130 | DURIKOSAMBI | CENGKARENG | https://docs.google.com/spreadsheets/d/12gem_gMMrXhnbHhl0jNwMG1RQDewmRvv9KzYA2Gwz7o/edit?usp=drive_link | MICOM P545 | Tap Setting | [101 empty] | Tap Setting | 2000-05-01 |  | 4,75 | 0,45 | - | - |  | 0,75 | 0,8 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.131 | DURIKOSAMBI | CENGKARENG | https://docs.google.com/spreadsheets/d/1XHeabcATmoiXzbczrISnDosADc7FLjSsKrEqPhYAPXI/edit?usp=drive_link | MICOM P545 | Tap Setting | [101 empty] | Tap Setting | 2000-05-01 |  | 4,75 | 0,45 | - | - |  | 0,75 | 0,8 | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.132 | DURIKOSAMBI | LMK | https://docs.google.com/spreadsheets/d/1OY291k7zDt6-eBiPIDrU8ww1TUMC9eLceEZx5LmCJY8/edit?usp=drive_link | MICOM P443 | Tap Setting |  | Enabled | Enabled | Disabled | - | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | -328596 | 150 kV / 100 V |  | 0,3 km | 0,02 ohm | 80,54 deg | 0.699 | -1,848 deg | 0,01 ohm | 5,19 ohm | 5,19 ohm | 0 s | 1,41 ohm | 5,77 ohm | 5,77 ohm | 0,8 s | 2,25 ohm | 6,41 ohm | 6,41 ohm | 1.2 s | [6 empty] | POR | 0 s |  |  | Enabled PoleDead | 40 s | Disabled | [5 empty] | Measured + MCB | Disabled |  | Not Active | [37 empty] | Tap Setting | -328596 |  | 4,68 A | 0,446 SI | Disabled | - |  | 0,78 A | 0,774 SI | Disabled | - | Disabled | Disabled | [17 empty] | Tap Setting Tanggal
PHT.133 | DURIKOSAMBI | GROGOL BARU | https://docs.google.com/spreadsheets/d/1QzJPlrFj79drqDLs5dDCiJUchmUilWCCDucJv-SEK7c/edit?usp=drive_link | 7SL87 | Tap Setting | [52 empty] | Tap Setting | [46 empty] | Tap Setting | -109450 |  | 6 A | 0.337 SI | Disabled | - |  | 1 A | 0.666 SI | Disabled | - | Disabled | Disabled | [20 empty] | Tap Setting Tanggal
PHT.134 | DURIKOSAMBI | GROGOL BARU | https://docs.google.com/spreadsheets/d/19Tta_Pgf8VceaAZbcgvL0zsjdPRefgPXwJDHrSeTZmw/edit?usp=drive_link | 7SL87 | Tap Setting | [52 empty] | Tap Setting | [46 empty] | Tap Setting | -109450 |  | 6 A | 0.337 SI | Disabled | - |  | 1 A | 0.666 SI | Disabled | - | Disabled | Disabled | [20 empty] | Tap Setting Tanggal
PHT.135 | DURIKOSAMBI | KEBON JERUK | https://docs.google.com/spreadsheets/d/139OjcSqWTXj4CMRzKc1diiAOWKn-VyltKPQWtqG5c5E/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  |  | 4000/5 A | 150 kV / 100 V | 10,2 km | 0,624 ohm | 72 deg | 0.772 | -17,23 deg |  | 1 A | 10 A | 30% | 150% | 0 | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | - | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,5 ohm | 72 deg | 12,3 ohm | 0,787 ohm | 72 deg | 17,57 ohm | 1,289 ohm | 72 deg | 25,1 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V |  | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 767132 |  | 0.276 In | 0.421 SI | Disabled | - |  | 0.046 Ien | 0.748 SI | Disabled | - | Disabled | Disabled | [17 empty] | Tap Setting Tanggal
PHT.136 | DURIKOSAMBI | KEBON JERUK | https://docs.google.com/spreadsheets/d/1oAq-UZ6qwvZAzGsVZiPZV6ZKqYY8WWNk875yfpl75LM/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | 2000/5 A | 150 kV / 100 V | 10,2 km | 0,31 ohm | 73,74 deg | 0.773 | -17,448 deg |  | 1 A | 4,6 A | 30% | 80% | 0 | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | Disabled | - | Disabled | - | Enabled PoleDead | 000011 (Z1 Z2) | Disabled | - | - |  | Measured + MCB | Disabled | Blocking |  | 0,25 ohm | 73,74 deg | 8,80 ohm | 0,42 ohm | 73,74 deg | 9,78 ohm | 0,71 ohm | 73,74 deg | 10,87 ohm |  | Not Active | - | - | - | - |  | - | - | Disabled | - | - | - | - | - | [14 empty] | Tap Setting | 2000-05-01 |  | 2,76 | 0,421 SI | - | - |  | 0,46 | 0,748 SI | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.137 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/1oe8ujMX_JkOGE_FO4BV0bOCyLh1uOKWT9sSxtYehSV4/edit?usp=drive_link | MICOM P545 | Tap Setting | [101 empty] | Tap Setting | -328596 |  | 5.52 A | 0.421 SI | Disable | - |  | 0.920 A | 0.748 SI | Disable | - | Disable | Disable | [17 empty] | Tap Setting Tanggal
PHT.138 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/1OrmBeE4PMXy4O0pfhkM3858KR7KEvptf74AklLTRUKU/edit?usp=drive_link | MICOM P546 | Tap Setting | [101 empty] | Tap Setting | -328596 |  | 5.52 A | 0.421 SI | Disable | - |  | 0.920 A | 0.748 SI | Disable | - | Disable | Disable | [17 empty] | Tap Setting Tanggal
PHT.139 | DURIKOSAMBI | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1p3nXTV53M5HPzYrRfyiqmUNPrTQsI37swmSfllTyM5Y/edit?usp=drive_link | RED670 | Tap Setting | 3000 / 5 A | 150 kV / 100 V |  | 0.2 x Ibase | 1.25 x Ibase | 2 x Ibase | 30% | 80% | 1 x Ibase | 1 s | 15% | 30% | Off | 0.01 s | - |  | 35.427 ohm/p |  |  |  |  | 36.87 deg |  |  |  | 0 s | 2.073 ohm | 0.316 ohm | 2.073 ohm | 0.316 ohm | 6.219 ohm | 0.568 ohm | 4.354 ohm/loop | 15.623 ohm/loop | 0 s |  | 5.706 ohm | 0.869 ohm | 17.118 ohm | 1.563 ohm | [5 empty] | Tap Setting | 11.983 ohm/loop | 22.319 ohm/loop | 0.4 s |  | 9.921 omh | 1.512 ohm | 29.764 ohm | 2.718 ohm | 20.835 ohm/loop | 31.884 ohm/loop | 1.6 s |  | On | Off |  | On |  | 0,165 ohm | 2,374 ohm | 0,225 ohm | 2,772 ohm | 0,395 ohm | 2,591 ohm | 0,71 ohm | 7,774 ohm | 2,1 km | [5 empty] | Off | - |  |  |  |  | Basic |  | 1 s | Not Used |  | On |  |  |  |  | Tap Setting | 10% Ubase | 0.167 Hz | 15 deg | [5 empty] | I>>: Tap Setting; tms: 3000 / 5 A; I>: 1.006 A; tms: 0.358 SI; I>: -; tms: - |  | 0.168 A | 0.659 SI | - | - | - | - | [8 empty] | Tap Setting Tanggal
PHT.140 | DURIKOSAMBI | DAAN MOGOT | https://docs.google.com/spreadsheets/d/1AQJHBJ3OULojzO979M0lmk6fExy2VRM0dQY2KNNRlrk/edit?usp=drive_link | RED670 | Tap Setting | 3000 / 5 A | 150 kV / 100 V |  | 0.2 x Ibase | 1.25 x Ibase | 2 x Ibase | 30% | 80% | 1 x Ibase | 1 s | 15% | 30% | Off | 0.01 s | - |  | 35.427 ohm/p |  |  |  |  | 36.87 deg |  |  |  | 0 s | 2.073 ohm | 0.316 ohm | 2.073 ohm | 0.316 ohm | 6.219 ohm | 0.568 ohm | 4.354 ohm/loop | 15.623 ohm/loop | 0 s |  | 5.706 ohm | 0.869 ohm | 17.118 ohm | 1.563 ohm | [5 empty] | Tap Setting | 11.983 ohm/loop | 22.319 ohm/loop | 0.4 s |  | 9.921 omh | 1.512 ohm | 29.764 ohm | 2.718 ohm | 20.835 ohm/loop | 31.884 ohm/loop | 1.6 s |  | On | Off |  | On |  | 0,165 ohm | 2,374 ohm | 0,225 ohm | 2,772 ohm | 0,395 ohm | 2,591 ohm | 0,71 ohm | 7,774 ohm | 2,1 km | [5 empty] | Off | - |  |  |  |  | Basic |  | 1 s | Not Used |  | On |  |  |  |  | Tap Setting | 10% Ubase | 0.167 Hz | 15 deg | [5 empty] | I>>: Tap Setting; tms: 3000 / 5 A; I>: 1.006 A; tms: 0.358 SI; I>: -; tms: - |  | 0.168 A | 0.659 SI | - | - | - | - | [8 empty] | Tap Setting Tanggal
PHT.141 | TANGERANG | CENGKARENG | https://docs.google.com/spreadsheets/d/1WDQtAVRWVcMBXEYNrTaze76UdxxwbbtRifsBtPVoLfE/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/5 A | 150kV/100V |  | - | - | 0,06 ohm/km | 1,29 / 0,667 | 9,23 km | 82 deg |  | On | 1 A | 0 | On | 10 A | On |  | On | 10 s |  | - |  | - |  | - |  | 0,949 ohm | 5,5 ohm | - | 0 s |  | 1,424 ohm | 10,834 ohm | - | 0,8 s |  | 2,943 ohm | 11,057 ohm | - | 1,6 s |  | 0,96 ohm | - | - | 0 s |  | 1,44 ohm | [5 empty] | Tap Setting | - | - |  | 2,966 ohm | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 2000/5 A |  | 3,75 A (sec) | 0,385 (IEC Norm Inverse) | - | - |  | 0,625 A (sec) | 0,64 (IEC Norm Inverse) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.142 | TANGERANG | CENGKARENG | https://docs.google.com/spreadsheets/d/1doRtkPD9VDq8BogaGbLM6VHPATJ25QnPRsghj_ox_Jc/edit?usp=drive_link | 7SL87 | Tap Setting | 2000/5 A | 150kV/100V |  | - | - | 0,06 ohm/km | 1,29 / 0,667 | 9,23 km | 82 deg |  | On | 1 A | 0 | On | 10 A | On |  | On | 10 s |  | - |  | - |  | - |  | 0,949 ohm | 5,5 ohm | - | 0 s |  | 1,424 ohm | 10,834 ohm | - | 0,8 s |  | 2,943 ohm | 11,057 ohm | - | 1,6 s |  | 0,96 ohm | - | - | 0 s |  | 1,44 ohm | [5 empty] | Tap Setting | - | - |  | 2,966 ohm | - | - | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 2000/5 A |  | 3,75 A (sec) | 0,385 (IEC Norm Inverse) | - | - |  | 0,625 A (sec) | 0,64 (IEC Norm Inverse) | - | - | - | - | [20 empty] | Tap Setting Tanggal
PHT.143 | TANGERANG | JATAKE BARU | https://docs.google.com/spreadsheets/d/1kLS7j2k8e3kLE9juhB96sMb6rlJJCvcUG1V-o0urseU/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/5 A |  | 0,514 ohm | 0,071 ohm | 1,543 ohm | 0,346 ohm | - | - | 6,87 km |  | 1 A | 1 | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 0,415 ohm | 0 s | 0,415 ohm | 0 s | 0,623 ohm | 0,4 s | 0,623 ohm | 0,4 s | 0,943 ohm | 1,6 s | 0,943 ohm | 1,6 s | 0,623 ohm | Z2 and Z3 | POTT |  | Disable | Enable |  | Disable | Disable | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000/5 A | Group 1 | 0,972 A (sec) | 0,355 (SI) | - | - | Group 1 | 0,162 A (sec) | 0,61 (SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.144 | TANGERANG | JATAKE BARU | https://docs.google.com/spreadsheets/d/1P5Pa3Gc7z8qCCGEBMA8aaHbBDhOp7gU8hFN4iD2QPTg/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/5 A |  | 0,514 ohm | 0,071 ohm | 1,543 ohm | 0,346 ohm | - | - | 6,87 km |  | 1 A | 1 | 1 | 1 |  | 0,678 ohm | -0,085 ohm | 82,15 deg | 0,415 ohm | 0 s | 0,415 ohm | 0 s | 0,623 ohm | 0,4 s | 0,623 ohm | 0,4 s | 0,943 ohm | 1,6 s | 0,943 ohm | 1,6 s | 0,623 ohm | Z2 and Z3 | POTT |  | Disable | Enable |  | Disable | Disable | Disable | Enable | Enable |  | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000/5 A | Group 1 | 0,972 A (sec) | 0,355 (SI) | - | - | Group 1 | 0,162 A (sec) | 0,61 (SI) | - | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.145 | ALAM SUTERA | CILEDUG | https://docs.google.com/spreadsheets/d/1JchLGM_8JGuJ2UJzWXbOd_34ffbV58XmDC4FQaoDEjw/edit?usp=drive_link | MICOM P543 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 3,25 km | 0,278 ohm | 76,971 deg | 1.015 | -37,193 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,222 ohm | 76,971 deg | 25,88 ohm | 0,755 ohm | 76,971 deg | 32,34 ohm | 1,332 ohm | 76,971 deg | 43,67 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,86 A | 0,415 (SI) | - | - | Group 1 | 0,14 A | 0,705 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.146 | ALAM SUTERA | CILEDUG | https://docs.google.com/spreadsheets/d/1mN0pVb9fDYDO035ti54lDmQmiSVbFuze2mvEuH3uui4/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | - | Enabled | - | - | - | - | - | - | - | Enabled | - | - | - | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 3,25 km | 0,278 ohm | 76,971 deg | 1.015 | -37,193 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,2 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,222 ohm | 76,971 deg | 25,88 ohm | 0,755 ohm | 76,971 deg | 32,34 ohm | 1,332 ohm | 76,971 deg | 40,43 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 0,86 A | 0,415 (SI) | - | - | Group 1 | 0,145 A | 0,7 (SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.147 | ALAM SUTERA | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/1gAeuD7_hhenIiw6X-N4CzMGpDDdgqFXuWll6Xg-r-fU/edit?usp=drive_link | RED670 | Tap Setting | 2000/1 A | 150kV/100V |  | 0.2 Ibase | 1.25 Ibase | 2 Ibase | 30% | 80% | 0.8 Ibase | 0.8 s | 15% | 30% | [13 empty] | 0 s | 0.875 ohm | 0.126 ohm | 0.875 ohm | 0.126 ohm | 2.624 ohm | 0.942 ohm | 1.837 ohm/loop | 24.548 ohm/loop | 0 s |  | 1.358 ohm | 0.196 ohm | 4.075 ohm | 1.463 ohm | [5 empty] | Tap Setting | 2.853 ohm/loop | 35.068 ohm/loop | 0.4 s |  | 3.223 ohm | 0.334 ohm | 9.668 ohm | 2.647 ohm | 6.767 ohm/loop | 50.098 ohm/loop | 1.6 s |  | On | Off |  | On | [11 empty] | PermOR | 0.035 |  |  | Off | - |  | On | UzsIZs | [6 empty] | On |  |  |  |  | Tap Setting | 10% | 2 Hz | 15 deg | [5 empty] | I>>: Tap Setting; tms: 2000/1 A; I>: 0,96 A; tms: 0,73 (SI); I>: -; tms: - |  | 0,16 A | 0,64 (SI) | - | - | - | - | [10 empty] | Tap Setting Tanggal
PHT.148 | ALAM SUTERA | SUMMARECON GADING SERPONG | https://docs.google.com/spreadsheets/d/1lfft6hnMraU0pzLBcTbd3Ilop914Sdx_QEoqrEMglk8/edit?usp=drive_link | RED670 | Tap Setting | 2000/1 A | 150kV/100V |  | 0.2 Ibase | 1.25 Ibase | 2 Ibase | 30% | 80% | 0.8 Ibase | 0.8 s | 15% | 30% | [13 empty] | 0 s | 0.875 ohm | 0.126 ohm | 0.875 ohm | 0.126 ohm | 2.624 ohm | 0.942 ohm | 1.837 ohm/loop | 24.548 ohm/loop | 0 s |  | 1.358 ohm | 0.196 ohm | 4.075 ohm | 1.463 ohm | [5 empty] | Tap Setting | 2.853 ohm/loop | 35.068 ohm/loop | 0.4 s |  | 3.223 ohm | 0.334 ohm | 9.668 ohm | 2.647 ohm | 6.767 ohm/loop | 50.098 ohm/loop | 1.6 s |  | On | Off |  | On | [11 empty] | PermOR | 3.5% |  |  | Off | - |  | On | UzsIZs | [6 empty] | On |  |  |  |  | Tap Setting | 10% | 2 Hz | 15 deg | [5 empty] | I>>: Tap Setting; tms: 2000/1 A; I>: 0,96 A; tms: 0,73 (SI); I>: -; tms: - |  | 0,16 A | 0,64 (SI) | - | - | - | - | [10 empty] | Tap Setting Tanggal
PHT.149 | KEMBANGAN | METLAND | https://docs.google.com/spreadsheets/d/19nEK6VrdppxmpRcAmCTt8rKTmgYKyWNNGtkXSIdXHSg/edit?usp=drive_link | 7SL87 | Tap Setting | 3200/5 A | 150kV/100V |  | 0,01 | 0,01 | 0,122 ohm/km | 0,076/0,667 | 2,609 km | 23,661 deg |  | On | 0,2 A | 0 s | On | 2 A | - |  | On | 10 s |  | - |  | - |  | 83,8 deg |  | 0,256 ohm | 9,145 ohm | 0,597 ohm | 0 s |  | 1,117 ohm | 17,875 ohm | 0,795 ohm | 0,4 s |  | 1,999 ohm | 18,34 ohm | 1,259 ohm | 1,6 s |  | - | - | 0,637 ohm | 0 s |  | - | [5 empty] | Tap Setting | - | 1,363 ohm |  | - | - | 2,355 ohm | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 474938 | Group 1 | CT: 2.584 A; *OCR: 0.428 SI; I>>: Group 1; tms: 0.431 A; *GFR: 0.75 SI | [20 empty] | Tap Setting Tanggal
PHT.150 | KEMBANGAN | METLAND | https://docs.google.com/spreadsheets/d/1NANLIITCPB2AS9A4bNKUEYQCK53VaAY8s-AKxthNW2A/edit?usp=drive_link | 7SL87 | Tap Setting | 3200/5 A | 150kV/100V |  | 0,01 | 0,01 | 0,122 ohm/km | 0,076/0,667 | 2,609 km | 23,661 deg |  | On | 0,2 A | 0 s | On | 2 A | - |  | On | 10 s |  | - |  | - |  | 83,8 deg |  | 0,256 ohm | 9,145 ohm | 0,597 ohm | 0 s |  | 1,117 ohm | 17,875 ohm | 0,795 ohm | 0,4 s |  | 1,999 ohm | 18,34 ohm | 1,259 ohm | 1,6 s |  | - | - | 0,637 ohm | 0 s |  | - | [5 empty] | Tap Setting | - | 1,363 ohm |  | - | - | 2,355 ohm | - |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | 474938 | Group 1 | CT: 2.584 A; *OCR: 0.428 SI; I>>: Group 1; tms: 0.431 A; *GFR: 0.75 SI | [20 empty] | Tap Setting Tanggal
PHT.151 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/167url0Bt7IuvsrwV3Wlt9uVQ-XMxTkI90p4S6ymZSlo/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 1000/5 A | 150kV/100V | 6,84 km | 0,105 ohm | 72,875 deg | 0.772 | -17,235 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,8 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,084 ohm | 72,875 deg | 4,02 ohm | 0,126 ohm | 72,875 deg | 5,02 ohm | 0,711 ohm | 72,875 deg | 6,28 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 1000/5 A | Group 1 | 4,75 A (sec) | 0,475(SI) | - | - | Group 1 | 0,75 A (sec) | 0,8(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.152 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/10N9GvgG9WxD1cMlm7VmLlzCOnnOdRyQ-HerOmnYTI_s/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 1000/5 A | 150kV/100V | 6,84 km | 0,105 ohm | 72,875 deg | 0.772 | -17,235 deg |  | 0,3 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,8 s | 1,6 s | - | - | - | - | Enable PoleDead | 000110 (Z2 Z3) | Enabled | 000110 | - |  | Measured + MCB | Disabled | - |  | 0,084 ohm | 72,875 deg | 4,02 ohm | 0,126 ohm | 72,875 deg | 5,02 ohm | 0,711 ohm | 72,875 deg | 6,28 ohm |  | Not Active | - | - | - | - |  | 52 V | 12 V | - | V< | Enabled | 15 deg | 6 V | 170 mHz | [14 empty] | Tap Setting | 1000/5 A | Group 1 | 4,75 A (sec) | 0,475(SI) | - | - | Group 1 | 0,75 A (sec) | 0,8(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.153 | KEMBANGAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1WKkODzeTLuKPPCL6z-OrPXqu14ChOAqt0CYzkiR76pM/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | -328596 | 150kV/100V | 9.87 km | 0.15 ohm | 72.87 deg | 0.772 | -17.234 |  | 0.93 A | 9.25 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 100 ms | Disabled | - | Enabled Pole Dead | 000011 (Z1, Z2) | Enabled | 000011 (Z1, Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 0.12 ohm | 72.87 deg | 4.38 ohm | 0.18 ohm | 72.87 deg | 4.86 ohm | 0.33 ohm | 72.87 deg | 5.41 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.154 | KEMBANGAN | NEW SENAYAN | https://docs.google.com/spreadsheets/d/1KpBWwyrMVRSi2zJV0aTTMb7s8_MI9zGmDUd10HaFGcs/edit?usp=drive_link | MICOM P546 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled |  | Tap Setting | -328596 | 150kV/100V | 9.87 km | 0.15 ohm | 72.87 deg | 0.772 | -17.234 |  | 0.93 A | 9.25 A | 30% | 80% | 0 s | Enabled | Disabled | Idiff Permit | Idiff Permit | Idiff Permit | Idiff Permit | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 100 ms | Disabled | - | Enabled Pole Dead | 000011 (Z1, Z2) | Enabled | 000011 (Z1, Z2) | - |  | Measured + MCB | Disabled | Blocking |  | 0.12 ohm | 72.87 deg | 4.38 ohm | 0.18 ohm | 72.87 deg | 4.86 ohm | 0.33 ohm | 72.87 deg | 5.41 ohm |  | Not Active | - | - | - | - |  | - | - | - | - | - | - | - | - | [14 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.155 | KEMBANGAN | PETUKANGAN | https://docs.google.com/spreadsheets/d/1t31_j4b_xKzqeXfrqTvB4JKvS1t73HS8y7kAAWPio5w/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/5A |  | 0.585 ohm | 0.093 ohm | 1.412 ohm | 0.395 ohm | 0 ohm | 0 ohm | 9.52 km |  | 1 A | 1 | Enabled | Disabled |  | 0.486 | -0.095 | 80.966 deg | 0.474 ohm | 0 s | 0.474 ohm | 0 s | 0.711 ohm | 0.4 s | 0.711 ohm | 0.4 s | 1.384 ohm | 1.6 s | 1.384 ohm | 1.6 s | 0.711 ohm | Z1, Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000-05-01 |  | 6 A (sec) | 0.44 SI | Disabled | - |  | 1 A | 0.77 SI | Disabled | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.156 | KEMBANGAN | PETUKANGAN | https://docs.google.com/spreadsheets/d/1zmIRITbtSDzGzlGqLszJtZFF3WSEBbEZ-yVWIca5FcI/edit?usp=drive_link | PCS-931 | Tap Setting | 150kV/100V | 2000/5A |  | 0.585 ohm | 0.093 ohm | 1.412 ohm | 0.395 ohm | 0 ohm | 0 ohm | 9.52 km |  | 1 A | 1 | Enabled | Disabled |  | 0.486 | -0.095 | 80.966 deg | 0.474 ohm | 0 s | 0.474 ohm | 0 s | 0.711 ohm | 0.4 s | 0.711 ohm | 0.4 s | 1.384 ohm | 1.6 s | 1.384 ohm | 1.6 s | 0.711 ohm | Z1, Z2 and Z3 | POTT |  | Disable | Enable | Disable | Disable | Disable | Disable | Enable | Enable | Disable | Enable | 1PAR/3PAR | [13 empty] | Tap Setting | 2000-05-01 |  | 6 A (sec) | 0.44 SI | Disabled | - |  | 1 A | 0.77 SI | Disabled | - | - | - | [12 empty] | Tap Setting Tanggal
PHT.157 | METLAND | KEMBANGAN | https://docs.google.com/spreadsheets/d/179_CH1lkXiKt-J1FguRux5erjkhXOw1ivyXQjf9OZbg/edit?usp=drive_link | 7SL87 | Tap Setting | 2000-01-01 | 150kV/100V |  | 0.01 miuF/km | 0.01 miuF/km | 0.383 Ohm/km | 0.076/0.667 | 2.609 km | 23.661 deg |  | ON | 0.2 A | 0 s | ON | 2 A | - |  | ON | 10 s |  |  |  | OFF |  |  |  | 0.799 Ohm | 28.577 Ohm | 1.867 Ohm | 0 s |  | 1.439 Ohm | 55.441 Ohm | 2.064 Ohm | 0.8 s |  | 2.953 Ohm | 56.696 Ohm | 3.319 Ohm | 1.6 s |  | On | 1.99 Ohm | 0 s | Yes |  |  |  |  | ON | 2.985 Ohm | 0.8 s | No | [6 empty] | Tap Setting |  |  |  | ON | 4.41 Ohm | 1.6 s | No | [5 empty] | 3 Ph Failure | ON | 3 s |  | Dist Z1 Dist Z2 | Dist Z1 | On | 0.05 s | [19 empty] | Tap Setting | 2000-01-01 |  | 0.827 A (sekunder) | 0.428 | OFF | - |  | 0.1378 A (sekunder) | 0.75 | OFF | - | [22 empty] | Tap Setting Tanggal
PHT.158 | METLAND | KEMBANGAN | https://docs.google.com/spreadsheets/d/1Cjyd2jz0C-e2Dwbb_jPFq1_UZiZcvp5FintVJFAL4q8/edit?usp=drive_link | 7SL87 | Tap Setting | 2000-01-01 | 150kV/100V |  | 0.01 miuF/km | 0.01 miuF/km | 0.383 Ohm/km | 0.076/0.667 | 2.609 km | 23.661 deg |  | ON | 0.2 A | 0 s | ON | 2 A | - |  | ON | 10 s |  |  |  | OFF |  |  |  | 0.799 Ohm | 28.577 Ohm | 1.867 Ohm | 0 s |  | 1.439 Ohm | 55.441 Ohm | 2.064 Ohm | 0.8 s |  | 2.953 Ohm | 56.696 Ohm | 3.319 Ohm | 1.6 s |  | On | 1.99 Ohm | 0 s | Yes |  |  |  |  | ON | 2.985 Ohm | 0.8 s | No | [6 empty] | Tap Setting |  |  |  | ON | 4.41 Ohm | 1.6 s | No | [5 empty] | 3 Ph Failure | ON | 3 s |  | Dist Z1 Dist Z2 | Dist Z1 | On | 0.05 s | [19 empty] | Tap Setting | 2000-01-01 |  | 0.827 A (sekunder) | 0.428 | OFF | - |  | 0.1378 A (sekunder) | 0.75 | OFF | - | [22 empty] | Tap Setting Tanggal
PHT.159 | METLAND | CILEDUG | https://docs.google.com/spreadsheets/d/1VEww-qRd52g7ojdAmLqyodaxK6VH3YTHkO81Ssy7KFM/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Group 1 | Enabled | Disabled | Enabled | Disabled |  | Enabled | Disabled | Disabled |  |  | Disabled |  |  |  | Enabled |  | Disabled |  | Tap Setting | 2000-01-01 | 150kv/100v | 5.356 km | 4.315 Ohm | 77.091 | 0.655 | 5.633 deg |  | 0.3 x In | 2.0 x In | 30 % | 150 % | 0 s | [12 empty] | 0s | 0.8 s | 1.6 s | POR | 100 ms | disabled | - | Enabled Pole Dead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measure + MCB | I diff |  |  | 3.452 Ohm | 77.091 deg | 26.81 Ohm | 5.178 Ohm | 77.091 deg | 33.51 Ohm | 5.512 Ohm | 77.091 deg | 41.9 Ohm |  | Not Active | [5 empty] | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 2000-01-01 |  | 0.827 A (sekunder) | 0.428 | OFF | - |  | 0.138 A (sekunder) | 0.75 | OFF | - | [19 empty] | Tap Setting Tanggal
PHT.160 | METLAND | CILEDUG | https://docs.google.com/spreadsheets/d/1bZ9XHIPIKVQQrKIzDS1Zvo5UXruEg1dK4wxT5CiejFs/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Group 1 | Enabled | Disabled | Enabled | Disabled |  | Enabled | Disabled | Disabled |  |  | Disabled |  |  |  | Enabled |  | Disabled |  | Tap Setting | 2000-01-01 | 150kv/100v | 5.356 km | 4.315 Ohm | 77.091 | 0.655 | 5.633 deg |  | 0.3 x In | 2.0 x In | 30 % | 150 % | 0 s | [12 empty] | 0s | 0.8 s | 1.6 s | POR | 100 ms | disabled | - | Enabled Pole Dead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measure + MCB | I diff |  |  | 3.452 Ohm | 77.091 deg | 26.81 Ohm | 5.178 Ohm | 77.091 deg | 33.51 Ohm | 5.512 Ohm | 77.091 deg | 41.9 Ohm |  | Not Active | [5 empty] | 52 V | 11.5 V |  | V< | Enabled | 15 deg | 6 V | 0.167 Hz | [14 empty] | Tap Setting | 2000-01-01 |  | 0.827 A (sekunder) | 0.428 | OFF | - |  | 0.138 A (sekunder) | 0.75 | OFF | - | [19 empty] | Tap Setting Tanggal
PHT.161 | SUMMARECON GADING SERPONG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/114A2IquyW1w_Elx655JgkryY-P1CmKq6elV4me_qcfw/edit?usp=drive_link | RED670 | Tap Setting | 2000/1A | 150kV/100V |  | 0,2 Ibase | 1,25 Ibase | 2 Ibase | 30% | 80% | 0,8 Ibase | - | 15% | 30% | - | - | - |  | - | - | - | - | - | - | - | - |  | 0 s | 0,875 ohm | 0,126 ohm |  |  | 2,624 ohm | 0,942 ohm | 1,837 ohm/loop | 24,548 ohm/loop | 0 s |  | 1,312 ohm | 0,189 ohm | 3,936 ohm | 1,413 ohm | [5 empty] | Tap Setting | 2,755 ohm/loop | 35,068 ohm/loop | 0,4 s |  | 8,051 ohm | 0,689 ohm | 24,152 ohm | 5,296 ohm | 16,906 ohm/loop | 50,098 ohm/loop | 1,6 s |  | On | Off |  | On |  | 0,266 ohm | 3,451 ohm | 0,259 ohm | 3,472 ohm | 0,157 ohm | 1,093 ohm | 1,177 ohm | 3,28 ohm | 7,168 km |  | PermOR | 0.035 |  |  | - | - |  | - | - |  | - | - | - | - |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting; tms: 2000/1A; I>: 0,96 A (sec); tms: 0,37(SI); I>: -; tms: - |  | 0,16 A (sec) | 0,62(SI) | - | - | - | - | [8 empty] | Tap Setting Tanggal
PHT.162 | SUMMARECON GADING SERPONG | ALAM SUTERA | https://docs.google.com/spreadsheets/d/1KWa9-PZ8g1_KvdAUqxqErVkca4WdxXGNVzL2ebE0Cpo/edit?usp=drive_link | RED670 | Tap Setting | 2000/1A | 150kV/100V |  | 0,2 Ibase | 1,25 Ibase | 2 Ibase | 30% | 80% | 0,8 Ibase | - | 15% | 30% | - | - | - |  | - | - | - | - | - | - | - | - |  | 0 s | 0,875 ohm | 0,126 ohm |  |  | 2,624 ohm | 0,942 ohm | 1,837 ohm/loop | 24,548 ohm/loop | 0 s |  | 1,312 ohm | 0,189 ohm | 3,936 ohm | 1,413 ohm | [5 empty] | Tap Setting | 2,755 ohm/loop | 35,068 ohm/loop | 0,4 s |  | 8,051 ohm | 0,689 ohm | 24,152 ohm | 5,296 ohm | 16,906 ohm/loop | 50,098 ohm/loop | 1,6 s |  | On | Off |  | On |  | 0,266 ohm | 3,451 ohm | 0,259 ohm | 3,472 ohm | 0,157 ohm | 1,093 ohm | 1,177 ohm | 3,28 ohm | 7,168 km |  | PermOR | 0.035 |  |  | - | - |  | - | - |  | - | - | - | - |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting; tms: 2000/1A; I>: 0,96 A (sec); tms: 0,37(SI); I>: -; tms: - |  | 0,16 A (sec) | 0,62(SI) | - | - | - | - | [8 empty] | Tap Setting Tanggal
PHT.163 | SUMMARECON GADING SERPONG | CURUG | https://docs.google.com/spreadsheets/d/1b89Yr8Sb190GQEFnO6G5zemn5Ku4ehDsvs7xwiBoSMc/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,7 km | 0,565 ohm | 81 | 0.861 | -31,18 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,452 ohm | 81 deg | 31,49 ohm | 1,886 ohm | 81 deg | 34,99 ohm | 6,253 ohm | 81 deg | 38,88 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 1,07 A (sec) | 0,37(SI) | - | - | Group 1 | 0,18 A (sec) | 0,65(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.164 | SUMMARECON GADING SERPONG | CURUG | https://docs.google.com/spreadsheets/d/19Al_PWI0Qw-CKb9WkhT3jHx0EY8L_6bgvAY0Rt5HkAY/edit?usp=drive_link | MICOM P545 | Tap Setting |  | Enabled | Enabled | Disabled | Enabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Disabled | Enabled | Disabled | Disabled | Disabled | Enabled | Enabled | Disabled |  | Tap Setting | 2000/1 A | 150kV/100V | 4,7 km | 0,565 ohm | 81 | 0.861 | -31,18 deg |  | 0,2 A | 2 A | 30% | 150% | 0 s | - | - | - | - | - | - | [6 empty] | 0 s | 0,4 s | 1,6 s | PUR | 0 s | Disabled | - | Enable PoleDead | 000011 (Z1 Z2) | Enabled | 000011 (Z1 Z2) | - |  | Measured + MCB | Disabled | - |  | 0,452 ohm | 81 deg | 31,49 ohm | 1,886 ohm | 81 deg | 34,99 ohm | 6,253 ohm | 81 deg | 38,88 ohm |  | Not Active | - | - | - | - |  | 52 V | 11,5 V | - | V< | Enabled | 15 deg | 6 V | 0,167 Hz | [14 empty] | Tap Setting | 2000/1 A | Group 1 | 1,07 A (sec) | 0,37(SI) | - | - | Group 1 | 0,18 A (sec) | 0,65(SI) | - | - | - | - | [17 empty] | Tap Setting Tanggal
PHT.165 | DURIKOSAMBI | GANDUL | https://docs.google.com/spreadsheets/d/19botCaaavxDBaf-vARrZlUhyojcuz9Rbbh_3pnyAtjE/edit?usp=drive_link | GRL 200 | Tap Setting |  | 767011 | 500kV/100V |  | On | 34.093 | 7.649 | 0.678 | 22.445 | 4.66 |  |  | Mho | 10 ohm | On | 25 ohm | 37 deg | 85 deg | 6.143 ohm | 0 s | 85 deg | 9.215 ohm | 0.8 s | 85 deg | 14.75 ohm | 1.2 s | Quad | 10 ohm | On | 25 ohm | 37 deg | 6.199 ohm | 85 deg | 21 ohm | 0 s | 9.179 ohm | 85 deg | 23.3 ohm | 0.8 s | 14.75 ohm | [5 empty] | 85 deg | 25.9 ohm | 1.2 s |  | PUP | 0.1 s |  | On | - | - | - | On | - | - | - | - | Off | - | - | - | - | - | - |  | On | 0.180 A | 1.80 A | 30% | 80% | *as site condition | 0 s | Off | Off | Non | Off | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.166 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/11BV33oYcBclStuVCuJZ7V96PSV7fhb_zHswq3X7Z2Io/edit?usp=drive_link | GRL 200 | Tap Setting |  | 767011 | 500kV/100V |  | On | 3.95 | 0.878 | 0.073 | 2.131 | 0.438 |  |  | Mho | 10 ohm | On | 23 ohm | 37 deg | 86 deg | 0.704 ohm | 0 s | 86 deg | 5.055 ohm | 0.4 s | 86 deg | 9.215 ohm | 1.6 s | Quad | 10 ohm | On | 23 ohm | 37 deg | 0.702 ohm | 86 deg | 21 ohm | 0 s | 5.036 ohm | 86 deg | 23.3 ohm | 0.4 s | 9.179 ohm | [5 empty] | 86 deg | 25.9 ohm | 1.6 s |  | PUP | 0.1 s |  | Off | - | - | - | On | - | - | - | - | Off | - | - | - | - | - | - |  | On | 0.225 A | 3 A | 30% | 80% | *as site condition | 0 s | Off | Off | Non | Off | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.167 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/14AlF79AraBJTeGh9qkIwk3s73H_7xgfBZyKW8Pwv9ns/edit?usp=drive_link | RED670 | Tap Setting | 767011 | 500kV/100V |  | 0.2 Ibase | 1.25 Ibase | 2 Ibase | 30% | 80% | 0.8 Ibase | 0 s | 15% | 30% | On | 0.25 s | - |  | 77.311 ohm/p | - | - | - | - | 36.87 deg | - | - |  | 0 s | 2.139 ohm | 0.188 ohm | 2.139 ohm | 0.188 ohm | 3.714 ohm | 0.573 ohm | 4.492 ohm | 34.094 ohm | 0 s |  | 2.709 ohm | 2.187 ohm | 5.423 ohm | 3.858 ohm | [5 empty] | Tap Setting | 5.688 ohm | 48.706 ohm | 0.4 s |  | 4.276 ohm | 4.03 ohm | 8.775 ohm | 7.019 ohm | 8.981 ohm | 69.58 ohm | 1.6 s |  | On | Off |  | On |  | 0.084 ohm | 1.088 ohm | 0.163 ohm | 1.33 ohm | 0.235 ohm | 2.674 ohm | 0.716 ohm | 4.643 ohm | 11.188 km |  | PermUR | 0.035 |  |  | On | Forward |  | On | UzslZs |  | - | - | - | - |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting | [15 empty] | Tap Setting Tanggal
PHT.168 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/1dzxuS-kaeIJKCwYQctaWZz4BLbJCilVkltEeraPu1d0/edit?usp=drive_link | RED670 | Tap Setting | 767011 | 500kV/100V |  | 0.2 Ibase | 1.25 Ibase | 2 Ibase | 30% | 80% | 0.8 Ibase | 0 s | 15% | 30% | On | 0.25 s | - |  | 77.311 ohm/p | - | - | - | - | 36.87 deg | - | - |  | 0 s | 2.139 ohm | 0.188 ohm | 2.139 ohm | 0.188 ohm | 3.714 ohm | 0.573 ohm | 4.492 ohm | 34.094 ohm | 0 s |  | 2.709 ohm | 2.187 ohm | 5.423 ohm | 3.858 ohm | [5 empty] | Tap Setting | 5.688 ohm | 48.706 ohm | 0.4 s |  | 4.276 ohm | 4.03 ohm | 8.775 ohm | 7.019 ohm | 8.981 ohm | 69.58 ohm | 1.6 s |  | On | Off |  | On |  | 0.084 ohm | 1.088 ohm | 0.163 ohm | 1.33 ohm | 0.235 ohm | 2.674 ohm | 0.716 ohm | 4.643 ohm | 11.188 km |  | PermUR | 0.035 |  |  | On | Forward |  | On | UzslZs |  | - | - | - | - |  | On |  |  |  |  | Tap Setting | 10% | 2 Hz | - | [5 empty] | I>>: Tap Setting | [15 empty] | Tap Setting Tanggal
PHT.169 | DURIKOSAMBI | GANDUL | https://docs.google.com/spreadsheets/d/1qoEK7SsH6Gy9AeMYtLG1S3L3Tnqz4qTUu2Axm6lwaoE/edit?usp=drive_link | PCS-931 | Tap Setting | 500kV/100V | 767011 |  | 7.649 | 0.678 | 22.445 | 4.66 | - | - | 34.093 |  |  | 1 | 1 | 0 |  | 0.68 | -0.12 | 85 | 6.143 | 0 | 6.143 | 0 | 9.215 | 0.8 | 9.215 | 0.8 | 14.75 | 1.2 | 14.75 | 1.2 | 9.215 | Z2 and Z3 | PUTT |  | Enable | Enable | Disable | Enable | Disable | Enable | Enable | [17 empty] | Tap Setting | [25 empty] | Tap Setting Tanggal
PHT.170 | DURIKOSAMBI | KEMBANGAN | https://docs.google.com/spreadsheets/d/1d_AKQc0gJyCAP-iRNKw2R-DeEPn-Yz7-7oaCY3nEewA/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | *fill at site | *fill at site | 0.2777 ohm/km | 1.67/0.476 | 3.95 km | 86 deg |  | On | 0.2 A | 0 s | On | 2 A | - |  | - | - |  | - |  | - |  | - |  | 0.702 ohm | 21 ohm | - | 0 s |  | 5.036 ohm | 23.3 ohm | - | 0.4 s |  | 9.179 ohm | 25.9 ohm | - | 1.6 s |  | 0.704 ohm | - | - | 0 s |  | 5.055 ohm | [5 empty] | Tap Setting | - | - |  | 9.215 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.171 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/16rxOCvaN_bd9qM1Pwedxa2TICeufOdtdjf2Vsd9RMcg/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | 0.014 uF/km | 0.014 uF/km | 0.191 ohm/km | 0.683/0.245 | 11.188 | 84.979 deg |  | On | 0.2 A | 0 s | On | 2 A | On |  | - | - |  | - |  | - |  | - |  | 1.711 ohm | 16.238 ohm | - | 0 s |  | 2.567 ohm | 34.157 ohm | - | 0.4 s |  | 3.421 ohm | 35.911 ohm | - | 1.6 s |  | 1.718 ohm | - | - | 0 s |  | 3.063 ohm | [5 empty] | Tap Setting | - | - |  | 5.246 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.172 | DURIKOSAMBI | MUARAKARANG | https://docs.google.com/spreadsheets/d/1l3DP_rtaIzlRxs49FWFlXOqB3M1q9iRdnGOS8iYSPRA/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | 0.014 uF/km | 0.014 uF/km | 0.191 ohm/km | 0.683/0.245 | 11.188 | 84.979 deg |  | On | 0.2 A | 0 s | On | 2 A | On |  | - | - |  | - |  | - |  | - |  | 1.711 ohm | 16.238 ohm | - | 0 s |  | 2.567 ohm | 34.157 ohm | - | 0.4 s |  | 3.421 ohm | 35.911 ohm | - | 1.6 s |  | 1.718 ohm | - | - | 0 s |  | 3.063 ohm | [5 empty] | Tap Setting | - | - |  | 5.246 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.173 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1E1ypR8s3N8wv1w3IrqS3cErlpvXo_TK3H_PDwmd-Dhk/edit?usp=drive_link | GRL 200 | Tap Setting |  | 767011 | 500kV/100V |  | On | 3.9 km | 0.866 omh | 0.072 ohm | 2.599 ohm | 0.54 ohm |  |  | Mho | 2 ohm | On | 34.163 ohm | 37 deg | 85.258 deg | 0.696 ohm | 0 s | 85.258 deg | 2.292 ohm | 0.4 s | 85.258 deg | 10.258 ohm | 1.6 s | Quad | 10 ohm | On | 28.868 ohm | 37 deg | 0.693 ohm | 85.258 deg | 16.058 ohm | 0 s | 2.2838 ohm | 85.258 deg | 32.192 ohm | 0.4 s | 10.218 ohm | [5 empty] | 85.258 deg | 32.9 ohm | 1.6 s |  | PUP | 0.1 s |  | - | - | - | - | On | - | - | - | - | - | - | - | - | - | - | - |  | On | 0.248 A | 1.654 A | 30% | 80% | On | 0 s | Off | Off | Non | Off | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.174 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/19fOcmB5XJClL6YUBYhyUzFlL8Q2bYuiKm-mpqiXpKmI/edit?usp=drive_link | GRL 200 | Tap Setting |  | 767011 | 500kV/100V |  | On | 3.9 km | 0.866 omh | 0.072 ohm | 2.599 ohm | 0.54 ohm |  |  | Mho | 2 ohm | On | 34.163 ohm | 37 deg | 85.258 deg | 0.696 ohm | 0 s | 85.258 deg | 2.292 ohm | 0.4 s | 85.258 deg | 10.258 ohm | 1.6 s | Quad | 10 ohm | On | 28.868 ohm | 37 deg | 0.693 ohm | 85.258 deg | 16.058 ohm | 0 s | 2.2838 ohm | 85.258 deg | 32.192 ohm | 0.4 s | 10.218 ohm | [5 empty] | 85.258 deg | 32.9 ohm | 1.6 s |  | PUP | 0.1 s |  | - | - | - | - | On | - | - | - | - | - | - | - | - | - | - | - |  | On | 0.248 A | 1.654 A | 30% | 80% | On | 0 s | Off | Off | Non | Off | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.175 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/14lQs5k6qf3O2swxH6HfjlTvqF_WgmJSAdpS-rJdRj_U/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | *fill at site | *fill at site | 0.2777 ohm/km | 1.67/0.476 | 3.95 km | 86 deg |  | On | 0.2 A | 0 s | On | 2 A | - |  | - | - |  | - |  | - |  | - |  | 0.702 ohm | 21 ohm | - | 0 s |  | 5.036 ohm | 23.3 ohm | - | 0.4 s |  | 9.179 ohm | 25.9 ohm | - | 1.6 s |  | 0.704 ohm | - | - | 0 s |  | 5.055 ohm | [5 empty] | Tap Setting | - | - |  | 9.215 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.176 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/1Vw3_-zf-Ka1O5vV0kmLORYNd18vCxnySllxGtUJVQIU/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | *fill at site | *fill at site | 0.2777 ohm/km | 1.67/0.476 | 3.95 km | 86 deg |  | On | 0.2 A | 0 s | On | 2 A | - |  | - | - |  | - |  | - |  | - |  | 0.702 ohm | 21 ohm | - | 0 s |  | 5.036 ohm | 23.3 ohm | - | 0.4 s |  | 9.179 ohm | 25.9 ohm | - | 1.6 s |  | 0.704 ohm | - | - | 0 s |  | 5.055 ohm | [5 empty] | Tap Setting | - | - |  | 9.215 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.177 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1WjPj7DDPLm96jjJtSsM-UfYyQXnLVY6ifcBsJvG4F5Q/edit?usp=drive_link | GRL 200 | Tap Setting |  | 2000-01-01 | 500kV/100V |  | On | 30.143 km | 3.3856 ohm | 0.3028 ohm | 10.1568 ohm | 2.1112 ohm |  |  | Mho | 2 ohm | On | 19 ohm | 10 deg | 84.892 deg | 2.721 ohm | 0 s | 84.892 deg | 4.074 ohm | 0.4 s | 84.892 deg | 13.279 ohm | 1.6 s | Quad | 10 ohm | On | 40 ohm | 10 deg | 2.709 ohm | 84.892 deg | 4.278 ohm | 0 s | 4.063 ohm | 84.892 deg | 8.323 ohm | 0.4 s | 12.94 ohm | [5 empty] | 84.892 deg | 10.998 ohm | 1.6 s |  | PUP | 0.1 s |  | - | - | - | - | On | - | - | - | - | Off | Off | - | - | - | - | - |  | On | 0.73 A | 3.6 A | 30% | 80% | On | 0.05 *as site needed | Off | Off | Non | Off | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.178 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1WjPj7DDPLm96jjJtSsM-UfYyQXnLVY6ifcBsJvG4F5Q/edit?usp=drive_link | GRL 200 | Tap Setting |  | 2000-01-01 | 500kV/100V |  | On | 30.143 km | 3.3856 ohm | 0.3028 ohm | 10.1568 ohm | 2.1112 ohm |  |  | Mho | 2 ohm | On | 19 ohm | 10 deg | 84.892 deg | 2.721 ohm | 0 s | 84.892 deg | 4.074 ohm | 0.4 s | 84.892 deg | 13.279 ohm | 1.6 s | Quad | 10 ohm | On | 40 ohm | 10 deg | 2.709 ohm | 84.892 deg | 4.278 ohm | 0 s | 4.063 ohm | 84.892 deg | 8.323 ohm | 0.4 s | 12.94 ohm | [5 empty] | 84.892 deg | 10.998 ohm | 1.6 s |  | PUP | 0.1 s |  | - | - | - | - | On | - | - | - | - | Off | Off | - | - | - | - | - |  | On | 0.73 A | 3.6 A | 30% | 80% | On | 0.05 *as site needed | Off | Off | Non | Off | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.179 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1P-3QKmuQg1MlHPY7ElDPJs6wpZuxCryWU1_mN8mpfng/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | *fill at site | *fill at site | 0.222 ohm/km | 1.67/0.476 | 3.9 km | 85.258 deg |  | On | 0.2 A | 0 s | On | 2 A | - |  | - | - |  | - |  | - |  | - |  | 0.693 ohm | 16.058 ohm | - | 0 s |  | 2.284 ohm | 32.192 ohm | - | 0.4 s |  | 10.218 ohm | 32.9 ohm | - | 1.6 s |  | 0.696 ohm | - | - | 0 s |  | 2.292 ohm | [5 empty] | Tap Setting | - | - |  | 10.258 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.180 | KEMBANGAN | DURIKOSAMBI | https://docs.google.com/spreadsheets/d/1MdZ6Enr6Y2q97JgUB9rThQurVRGjooKTns1xEaxtN7E/edit?usp=drive_link | 7SL87 | Tap Setting | 767011 | 500kV/100V |  | *fill at site | *fill at site | 0.222 ohm/km | 1.67/0.476 | 3.9 km | 85.258 deg |  | On | 0.2 A | 0 s | On | 2 A | - |  | - | - |  | - |  | - |  | - |  | 0.693 ohm | 16.058 ohm | - | 0 s |  | 2.284 ohm | 32.192 ohm | - | 0.4 s |  | 10.218 ohm | 32.9 ohm | - | 1.6 s |  | 0.696 ohm | - | - | 0 s |  | 2.292 ohm | [5 empty] | Tap Setting | - | - |  | 10.258 ohm | - | - |  |  | - | - | - |  | - | - | - | - | [30 empty] | Tap Setting | [33 empty] | Tap Setting Tanggal
PHT.181 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/1wCwDFJw1G5416feNkOtOGu-M8US49ozY3izaUqroNSM/edit?usp=drive_link | GRL 200 | Tap Setting |  | 767011 | 500kV/100V |  | On | 3.95 km | 8.410 ohm | 0.576 ohm | 25.216 ohm | 5.376 ohm |  |  | Mho | 10 ohm | On | 23 ohm | 37 deg | 86 deg | 6.743 ohm | 0 s | 86 deg | 11.040 ohm | 0.4 s | 86 deg | 27.32 ohm | 1.6 s | Quad | 10 ohm | On | 23 ohm | 37 deg | 6.728 ohm | 86 deg | 21 ohm | 0 s | 10.922 ohm | 86 deg | 23.3 ohm | 0.4 s | 26.807 ohm | [5 empty] | 86 deg | 25.9 ohm | 1.6 s |  | PUP | 0.1 s |  | ON | - | 0.1 s | On | On | - | - | - | - | Off | Off | - | - | - | - | - |  | On | 0.3 A | 3 A | 30% | 80% | *as site needed | 0 s | Off | Off | Non | On | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.182 | KEMBANGAN | BALARAJA | https://docs.google.com/spreadsheets/d/1RfqRnc2Jhl0Y7bVuY9D3GW9iy9SNbg3jPmqU5fFCaAQ/edit?usp=drive_link | GRL 200 | Tap Setting |  | 767011 | 500kV/100V |  | On | 3.95 km | 8.410 ohm | 0.576 ohm | 25.216 ohm | 5.376 ohm |  |  | Mho | 10 ohm | On | 23 ohm | 37 deg | 86 deg | 6.743 ohm | 0 s | 86 deg | 11.040 ohm | 0.4 s | 86 deg | 27.32 ohm | 1.6 s | Quad | 10 ohm | On | 23 ohm | 37 deg | 6.728 ohm | 86 deg | 21 ohm | 0 s | 10.922 ohm | 86 deg | 23.3 ohm | 0.4 s | 26.807 ohm | [5 empty] | 86 deg | 25.9 ohm | 1.6 s |  | PUP | 0.1 s |  | ON | - | 0.1 s | On | On | - | - | - | - | Off | Off | - | - | - | - | - |  | On | 0.3 A | 3 A | 30% | 80% | *as site needed | 0 s | Off | Off | Non | On | Non | 1P | [19 empty] | Tap Setting | [30 empty] | Tap Setting Tanggal
PHT.183 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1RQQoBbTf6BB1zJJy3Tv0m3ZIQD7fQpwRUIMkuh2oK2w/edit?usp=drive_link | PCS-931 | Tap Setting | [59 empty] | Tap Setting | [25 empty] | Tap Setting Tanggal
PHT.184 | KEMBANGAN | GANDUL | https://docs.google.com/spreadsheets/d/1RQQoBbTf6BB1zJJy3Tv0m3ZIQD7fQpwRUIMkuh2oK2w/edit?usp=drive_link | PCS-931 | Tap Setting | [59 empty] | Tap Setting | [25 empty] | Tap Setting Tanggal

## OCR_KOPEL (hidden)
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | SIRKIT | BUSPRO AKTIF? | RATIO CT | HELPER ASET |  |  |  | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | OCR | [9 empty] | OCR
[8 empty] | GI/GIS | BAY | CT | [6 empty] | TAP SET | SETTING (TAP SETTING) | [8 empty] | TAP SET | SETTING (TERPASANG)
[18 empty] | In | Iset OC | tms OC | char OC | Iset GF | tms GF | char GF | PDF | TGL |  | In | Iset OC | tms OC | char OC | Iset GF | tms GF | char GF | TGL | FILE
[10 empty] | PRI | SEC
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
KPL.01 | 1 | ULTG ANGKE | GI 150KV ANGKE | KOPEL BUS 150kV |  | YA | 4000/5 | GI 150KV ANGKE | KOPEL BUS 150kV | 4000 | 5 | GE | MICOM P142 | 34421636/04/18 | Numerik |  |  | 5 | 6 | 0.432 | SI | 2 | 0.662 | SI | Tap Setting Official GI Angke bay Kopel.pdf | 2019-03-01 |  | 5 | 6 | 0.45 | SI | Disabled | Disabled | -
KPL.02 | 2 | ULTG ANGKE | GI 150KV DADAP | KOPEL BUS 150kV |  | YA | 4000/1 | GID 150KV DADAP | KOPEL BUS 150kV | 4000 | 1 | GE | MICOM P841 | 34465151/05/18 | Numerik | 2021 |  | 1 | 1.2 | 0.432 | SI | blok | blok | blok | Setting Proteksi Trafo dan Kopel.pdf | 2020-02-20 |  | 1 | 1.2 | 0.432 | SI | Disabled | Disabled | -
KPL.03 | 3 | ULTG ANGKE | GIS 150kV DAAN MOGOT | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV DAAN MOGOT | KOPEL BUS 150kV | 4000 | 1 | ABB | REF615 | 1YM192742771 | Numerik | 2019 |  | 1 |  |  | SI |  |  | blok |  |  |  | 1 | 1.2 | 0.432 | SI | Disabled | Disabled | -
KPL.04 | 4 | ULTG ANGKE | GIS 150KV GROGOL | KOPEL BUS 150kV |  | YA | 2000/1 | GIS 150KV GROGOL | KOPEL BUS 150kV | 2000 | 1 | SCHNEIDER | MICOM P142 | 39732197/03/20 | Numerik | 2022 |  | 1 | 1.2 | 0.527 | SI | blok | blok | blok | 2022 03 01 - Tap Setting GIS Grogol bay Kopel.pdf | 2022-03-01 |  | 1 | 1.2 | 0.525 | SI | Disabled | Disabled | -
KPL.05 | 5 | ULTG ANGKE | GIS 150KV GROGOL BARU | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV GROGOL BARU | KOPEL BUS 150kV | 4000 | 1 | SIEMENS | 7SJ82 | BM1804004003 | Numerik | 2019 |  | 1 | 1.2 | 0.43 | SI | blok | blok | blok | Official Kopel Grogol II.pdf | 2019-10-23 |  | 1 | 1.2 | 0.43 | SI | Disabled | Disabled | -
KPL.06 | 6 | ULTG ANGKE | GIS 150KV KEBON JERUK | KOPEL BUS 150kV |  | YA | 2000/5 | GIS 150KV KEBON JERUK | KOPEL BUS 150kV | 2000 | 5 | ABB | REF615 | 1VHR91359915 | Numerik | 2021 |  | 5 |  |  | SI |  |  | blok |  |  |  | 5 | 6 | 0.99 | SI | Disabled | Disabled | -
KPL.07 | 7 | ULTG ANGKE | GIS 150KV NEW SENAYAN | KOPEL BUS 150kV |  | YA | 2000/1 | GIS 150KV NEW SENAYAN | KOPEL BUS 150kV | 2000 | 1 | NR | PCS-9611S | NRJB2145332510092 | Numerik | 2025 |  | 1 | 1.2 | 0.588 | SI | blok | blok | blok | GIS NEW SENAYAN OCR KOPEL ttd.pdf | 2025-08-05 |  | 1 | 1.2 | 0.588 | SI | Disabled | Disabled | -
KPL.08 | 8 | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV PANTAI INDAH KAPUK | KOPEL BUS 150kV | 4000 | 1 | SIEMENS | 7SJ63 | BF1603500940 | Numerik | 2016 |  | 1 | 1.2 | 0.46 | SI | blok | blok | blok | GIS PIK .pdf | 2016-01-22 |  | 1 | 1.2 | 0.46 | SI | 0.4 | 0.71 | SI
KPL.09 | 9 | ULTG ANGKE | GIS 150KV TOMANG | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV TOMANG | KOPEL BUS 150kV | 4000 | 1 | ALSTOM | MICOM P143 | 39704709/07/19 | Numerik | 2021 |  | 1 | 1.2 | 0.342 | SI | blok | blok | blok | official tap setting OCR kopel Tomang .pdf | 2019-10-31 |  | 1 | 1.2 | 0.34 | SI | Disabled | Disabled | -
KPL.10 | 10 | ULTG ANGKE | GIS 150KV ULUJAMI | KOPEL BUS 150kV |  | YA | 2000/1 | GIS 150KV ULUJAMI | KOPEL BUS 150kV | 2000 | 1 | GE | MICOM P143 | 34724746/03/19 | Numerik | 2021 |  | 1 | 1.2 | 0.588 | SI | blok | blok | blok | 154. Buspro, CBF dan OCR Kopel NEW Senayan II (1).pdf | 2020-11-11 |  | 1 | 1.2 | 0.59 | SI | Disabled | Disabled | -
KPL.11 | 11 | ULTG CITRA RAYA | GI 150KV CURUG | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV CURUG | KOPEL BUS 150kV | 4000 | 1 | SCHNEIDER | MICOM P142 | 39731745/04/20 | Numerik | 2021 |  | 1 |  |  | SI |  |  | blok |  |  |  | 1 | 1.2 | 0.435 | SI | Disabled | Disabled | -
KPL.12 | 12 | ULTG CITRA RAYA | GI 150KV GAJAH TUNGGAL | KOPEL BUS 150kV |  | YA | 2000/1 | GI 150KV GAJAH TUNGGAL | KOPEL BUS 150kV | 2000 | 1 | ABB | REF615E | 1VHR91344403 | Numerik | 2021 |  | 1 | 1.2 | 0.59 | SI | 0.4 | 0.82 | SI | 20171123_Tap Setting Kopel & Buspro GI Gajah Tunggal.pdf | 2017-11-23 |  | 1 | 1.2 | 0.59 | SI | Disabled | Disabled | -
KPL.13 | 13 | ULTG CITRA RAYA | GI 150KV ITS | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV ITS | KOPEL BUS 150kV | 4000 | 1 | SIEMENS | 7SJ82 | BM2102004945 | Numerik | 2021 |  | 1 |  |  | SI |  |  | blok |  |  |  | 1 | 0 | 0 | SI | Disabled | Disabled | -
KPL.14 | 14 | ULTG CITRA RAYA | GI 150KV JATAKE | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV JATAKE | KOPEL BUS 150kV | 4000 | 1 | SCHNEIDER | MICOM P142 | 39732205/03/20 | Numerik | 2021 |  | 1 | 1.2 | 0.358 | SI | blok | blok | blok | 2022 02 16 - Rev01.Tap Setting OCR GI Jatake bay Kopel.pdf | 2022-02-16 |  | 1 | 1.2 | 0.36 | SI | Disabled | Disabled | -
KPL.15 | 15 | ULTG CITRA RAYA | GI 150KV MAXIMANGANDO | KOPEL BUS 150kV |  | YA | 2000/5 | GI 150KV MAXIMANGANDO | KOPEL BUS 150kV | 2000 | 5 | SCHNEIDER | MICOM P142 | 39732578/04/20 | Numerik | 2021 |  | 5 | 6 | 0.51 | SI | blok | blok | blok | 2022 01 20 - Tap Setting GI Maximangando bay Kopel.pdf | 2022-01-21 |  | 5 | 6 | 0.5 | SI | Disabled | Disabled | -
KPL.16 | 16 | ULTG CITRA RAYA | GI 150KV SINDANG JAYA | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV SINDANG JAYA | KOPEL BUS 150kV | 4000 | 1 | NR | PCS-9611 |  | Numerik | 2021 |  | 1 | 1.2 | 0.432 | SI | blok | blok | blok | Kopel Tangerang Baru II_PCS9611.pdf | 2020-05-13 |  | 1 | 1.2 | 0.432 | SI | Disabled | Disabled | -
KPL.17 | 17 | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV TANGERANG BARU | KOPEL BUS 150kV | 4000 | 1 | 11: AREVA; 12: MICOM P141; 13: 3375741/03/09; 14: Numerik; 17: 1; 20: SI; 23: blok; 27: 1; 28: 1.2; 29: 0.505; 30: SI; 31: 0.4; 32: 0.505; 33: SI
KPL.18 | 18 | ULTG CITRA RAYA | GI 150KV TELUK NAGA | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV TELUK NAGA | KOPEL BUS 150kV | 4000 | 1 | 11: AREVA; 12: MICOM P141; 13: 3375745/05/09; 14: Numerik; 17: 1; 20: SI; 23: blok; 27: 1; 28: 1.2; 29: 0.8; 30: SI; 31: 0.4; 32: 1.2; 33: SI
KPL.19 | 19 | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV JATAKE BARU | KOPEL BUS 150kV | 4000 | 1 | NR | PCS-9611 | NRJB21322819B0090 | Numerik | 2021 |  | 1 | 1.2 | 0.325 | SI | blok | blok | blok | GI Jatake II bay KOPEL_PCS9611.pdf | 2020-04-26 |  | 1 | 1.2 | 0.325 | SI | Disabled | Disabled | -
KPL.20 | 20 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | KOPEL BUS 150kV |  | YA | 4000/5 | GI 150KV CENGKARENG | KOPEL BUS 150kV | 4000 | 5 | AREVA | MICOM P141 | 3375739/05/09 | Numerik | 2012 |  | 5 | 6 | 0.482 | SI | blok | blok | blok | 2023 07 10 - Tap Setting GI Cengkareng bay Kopel.Rev01.pdf | 2023-07-10 |  | 5 | 6 | 0.48 | SI | Disabled | Disabled | -
KPL.21 | 21 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV CENGKARENG BARU | KOPEL BUS 150kV | 4000 | 1 | ALSTOM | MICOM P14D | 33980261/02/14 | Numerik | 2018 |  | 1 | 1.2 | 0.301 | SI | blok | blok | blok | 2022 03 08 - Tap Setting GI Cengkareng Baru bay Kopel.pdf | 2022-03-08 |  | 1 | 1.2 | 0.43 | SI | Disabled | Disabled | -
KPL.22 | 22 | ULTG DURIKOSAMBI | GI 150KV CILEDUG | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV CILEDUG | KOPEL BUS 150kV | 4000 | 1 | SCHNEIDER | MICOM P142 |  | Numerik | 2021 |  | 1 | 1.2 | 0.34 | SI | blok | blok | blok | 2021 03 18 - Tap Setting GI Ciledug bay Kopel - Rev01.pdf | 2021-03-29 |  | 1 | 1.2 | 0.34 | SI | Disabled | Disabled | -
KPL.23 | 23 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | KOPEL BUS#1 150kV | #1 | YA | 4000/5 | GI 150KV DURIKOSAMBI | KOPEL BUS#1 150kV | 4000 | 5 | NR | PCS 9611S | NRJB2145332510108 | Numerik | 2025 |  | 5 | 6 | 0.432 | SI | blok | blok | blok | GI DURIKOSAMBI BAY KOPEL.pdf | 2025-09-25 |  | 5 | 6 | 0.432 | SI | Disabled | Disabled | -
KPL.24 | 24 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | KOPEL BUS#2 150kV | #2 | YA | 4000/5 | GI 150KV DURIKOSAMBI | KOPEL BUS#2 150kV | 4000 | 5 | NR | PCS 9611S | NRJB2145332510105 | Numerik | 2025 |  | 5 | 6 | 0.432 | SI | blok | blok | blok | GI Durikosambi_OCR Kopel #2 (Kontrak 0029_2025).pdf | 2025-10-08 |  | 5 | 6 | 0.432 | SI | Disabled | Disabled | -
KPL.25 | 25 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | BUS SECTION#1 150kV | A | YA | 4000/5 | GI 150KV DURIKOSAMBI | BUS SECTION #1 150kV | 4000 | 5 | ABB | REF 615 |  | Numerik | 2019 |  | 5 | 6 | 0.43 | SI | 1 | 0.43 | SI |  |  |  | 5 | 1.2 | 0.43 | SI | 0.2 | 0.82 | SI
KPL.26 | 26 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | BUS SECTION#2 150kV | B | YA | 4000/5 | GI 150KV DURIKOSAMBI | BUS SECTION #2 150kV | 4000 | 5 | ABB | REF 615 | 1VHR91419727 | Numerik | 2018 |  | 5 | 6 | 0.43 | SI | 1 | 0.82 | SI |  |  |  | 5 | 1.2 | 0.43 | SI | 0.2 | 0.82 | SI
KPL.27 | 27 | ULTG DURIKOSAMBI | GI 150KV TANGERANG | KOPEL BUS 150kV |  | YA | 4000/1 | GI 150KV TANGERANG | KOPEL BUS 150kV | 4000 | 1 | SCHNEIDER | MICOM P142 | 39733532/04/20 | Numerik | 2021 |  | 1 | 1.2 | 0.482 | SI | 0.2 | 0.682 | SI | 2023 08 01 - Tap Setting GI Tangerang bay Kopel.pdf | 2023-08-01 |  | 1 | 1.2 | 0.48 | SI | Disabled | Disabled | -
KPL.28 | 28 | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV ALAM SUTERA | KOPEL BUS 150kV | 4000 | 1 | ALSTOM | MICOM P141 | 32065266/02/12 | Numerik |  |  | 1 | 1.2 | 0.287 | SI | blok | blok | blok | 2022 05 19 - Tap Setting GIS Alam Sutera bay Kopel.pdf | 2022-05-19 |  | 1 | 1.2 | 0.285 | SI | Disabled | Disabled | -
KPL.29 | 29 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | KOPEL BUS 150kV |  | YA | 4000/5 | GIS 150KV KEMBANGAN | KOPEL BUS 150kV | 4000 | 5 | SCHNEIDER | MICOM P142 | 39732188/03/20 | Numerik | 2022 |  | 5 |  |  | SI |  |  | blok |  |  |  | 5 | 5 | 0.3 | SI | Disabled | Disabled | -
KPL.30 | 30 | ULTG DURIKOSAMBI | GIS 150KV METLAND | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV METLAND | KOPEL BUS 150kV | 4000 | 1 | SIEMENS | 7SJ82 | BM1801000397 | Numerik | 2022 |  | 1 | 1 | 0.432 | SI | blok | blok | blok | tap setting Kembangan II - OCR kopel 7SJ82.pdf | 2022-01-05 |  | 1 | 1.2 | 0.43 | SI | Disabled | Disabled | -
KPL.31 | 31 | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | KOPEL BUS 150kV |  | YA | 4000/1 | GIS 150KV SUMMARECON GADING SERPONG | KOPEL BUS 150kV | 4000 | 1 | ABB | REF615E | 1VHR91392165 | Numerik | 2019 |  | 1 | 1.2 | 0.482 | SI | blok | blok | blok | 20190507_SUMMARECON_KOPEL.pdf | 2019-05-07 |  | 1 | 1.2 | 0.48 | SI | Disabled | Disabled | -

## DV_HELPER_KPL (hidden)
ID | GI/GIS | BAY | SRC |  | LISTING
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
|  |  | https://docs.google.com/spreadsheets/d/1XDq28xtmisJaeHPS9ffm2tuePAU-2tLCTC03H6AjbM8/edit?usp=drive_link |  | Parameter | CT | OCR HV | I> | tms | I>> | tms | GFR HV | Ie> | tms |  | Cek seluruh elemen seperti Overvoltage, CB Fail pada relay. Apakah sudah disable seluruhnya? | Cek Disturbance Record, apakah seluruhnya sudah dikonfigurasikan? | Catatan :
KPL.01 | GI 150KV ANGKE | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1XDq28xtmisJaeHPS9ffm2tuePAU-2tLCTC03H6AjbM8/edit?usp=drive_link |  | Setting Terpasang | 767132 |  | 6 | 0.45 | BLOCK |  |  | - | -
KPL.02 | GI 150KV DADAP | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/18wK1pLR2ZitraOGWqnICuuA3-XMqtsJrxSHmCnXn_b0/edit?usp=drive_link |  | Setting Terpasang | 4000/1A | Group 1 | 1,2 A (sec) | 0,432(SI) | Disable | Disable | Group 1 | Disable | Disable
KPL.03 | GIS 150kV DAAN MOGOT | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1k2TDKbalDtxggnUOjHdYoWyKH0SREZ2pKudCLSn6czg/edit?usp=drive_link |  | Setting Terpasang | 4000/1A | Group 1 | 1,2 | 0,432 SI | Disable | Disable | Group 1 | Disable | Disable
KPL.04 | GIS 150KV GROGOL | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1R9vv0NfDSXTAVLDo6WbZ3am2fQI2ZuRZn83a1M6X9wE/edit?usp=drive_link |  | Setting Terpasang | 2000/1 A |  | 1,2 A (sec) | 0,525 (SI) | Disable | - |  | Disable | -
KPL.05 | GIS 150KV GROGOL BARU | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/10_waPTLQt3tYJw-UtHcyjpYPNLpltXLWuRu6FpgXMOo/edit?usp=drive_link |  | Setting Terpasang | 4000/1 A | Group 1 | 1,2 A | 0,43 (SI) | - | - | Group 1 | Blocked | Blocked
KPL.06 | GIS 150KV KEBON JERUK | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1N10es7VrHP5s8KZW8epsqfbur6hNiGDRp5uw9fU2S-c/edit?usp=drive_link |  | Setting Terpasang | 2000/5 A |  | 6 A | 0.99 | - | - |  | Block | Block
KPL.07 | GIS 150KV NEW SENAYAN | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1qYJO8J9y52g5yUqzA7rIRPivgy747Q3kgJEHQGaOqso/edit?usp=drive_link |  | Setting Terpasang | 2000/1 A | Group 1 | 1.2 A | 0.588 SI | Disable | Disable |  | Disable | Disable
KPL.08 | GIS 150KV PANTAI INDAH KAPUK | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1lA2HC6DRgwhjUw1VTfbMTmfrNyBEnZDUDI0zQqQKD0o/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1.2 A | 0.46 (SI) | BLOCK |  |  | 0.4 A | 0.71 (SI)
KPL.09 | GIS 150KV TOMANG | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1L2o338NsRL9oI1y32kO1h8qeZfvFrb_ukFRG2eH4Ibw/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1,2 A | 0,34 | BLOCK |  | BLOCK | BLOCK | BLOCK
KPL.10 | GIS 150KV ULUJAMI | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/18ZY97NrakLszL43GVXhc6Nd0EZzQRqsIbthRtQQ96mk/edit?usp=drive_link |  | Setting Terpasang | 2000/1 A | Group 1 | 1,2 A | 0.590 | - | - | Disable | Disable | Disable
KPL.11 | GI 150KV CURUG | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1O6bDaQsr76NEq9RAXfoS0xJ9hkfDPTDmZ_O4JSmxwk0/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1.2 A | 0.435 | BLOCK |  |  | - | -
KPL.12 | GI 150KV GAJAH TUNGGAL | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1_rOQVB7shOFqgfO1s2xQ6NjaweiwAjdHXoUcbzd201k/edit?usp=drive_link |  | Setting Terpasang | 2000-01-01 |  | 1.2 | 0.59 | - | - |  | - | -
KPL.13 | GI 150KV ITS | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/103j0jPpw0--tl-3Fn0Uzd0B_7v6TMcuXalnvAOyhvuc/edit?usp=drive_link |  | Setting Terpasang
KPL.14 | GI 150KV JATAKE | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1YLY1i33KBE9ZdMRD_QgItYXreynGkppGcj1PpAeCxxI/edit?usp=drive_link |  | Setting Terpasang | 4000/1A | Group 1 | 1,2 A (sec) | 0,36 (SI) | - | - | Group 1 | Blocked | Blocked
KPL.15 | GI 150KV MAXIMANGANDO | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/10tWfX8iQRCjfGjSec78nNZ3DrZUodWlbrIQTdbz7L2k/edit?usp=drive_link |  | Setting Terpasang | 2000/5 A | Group 1 | 6 | 0.5 | - | - | Group 1 | Disabled | Disabled
KPL.16 | GI 150KV SINDANG JAYA | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1WNh58mBQkV0ud5u0Ga4c2qy_MJp-kydT-CcAmXeaDb0/edit?usp=drive_link |  | Setting Terpasang | 4000/1A | 50/51P4 | 1,2 A (sec) | 0,432 (SI) | - | - | Group 1 | Blocked | Blocked
KPL.17 | GI 150KV TANGERANG BARU | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/196Ctl_WTYIy-h0Ym6JRaxBKhj-N9UPZZvlvHOKoRqJY/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1.2 A | 0.505 | BLOCK |  |  | 0.4 | 0.505
KPL.18 | GI 150KV TELUK NAGA | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1O7JKtEzE7RT5YsuNmGqqbWrOcj5FHAVlK8muHrA482w/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1.2 A | 0.8 | BLOCK |  |  | 0.4 | 1.2
KPL.19 | GIS 150KV JATAKE BARU | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1H-AXDvCF10Pnw5qhgIHwrgxRYjqAM_3P1YtPgz0iZbg/edit?usp=drive_link |  | Setting Terpasang | 4000/1A | Group 1 | 1,2 A (sec) | 0,325(SI) | - | - | Group 1 | Blocked | Blocked
KPL.20 | GI 150KV CENGKARENG | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/12TkHBBVWVNTTxyV2Y1gOhqxTSxAJHVbmpBglIoX1ttY/edit?usp=drive_link |  | Setting Terpasang | 4000/5 A |  | 6 | 0,48 |  |  |  | DISABLED | DISABLED
KPL.21 | GI 150KV CENGKARENG BARU | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/18qzixkQto5g_cR8tXtnrvJtQJ5_WcfvkVb6dexLkE7M/edit?usp=drive_link |  | Setting Terpasang | 4000/1 A |  | 1,2 | 0,43 |  |  |  | DISBALED | DISABLED
KPL.22 | GI 150KV CILEDUG | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1b8Vi5GyJprefD8KpXnY72Ibw9PQDBN1iqCHnJS2WhzA/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1,2 | 0,34 |  |  |  | blocked | blocked
KPL.23 | GI 150KV DURIKOSAMBI | KOPEL BUS#1 150kV | https://docs.google.com/spreadsheets/d/1NanELCcvrD2WuDc2TBuIG3i9PViwjuMGlf9EtdODhRE/edit?usp=drive_link |  | Setting Terpasang | 767132 |  | 6 A | 0.432 SI | Disabled | - |  | Disabled | -
KPL.24 | GI 150KV DURIKOSAMBI | KOPEL BUS#2 150kV | https://docs.google.com/spreadsheets/d/15SxiqbbP1lTytNlTBplbn5zwgBPYT1hNxfJ6ysikVCA/edit?usp=drive_link |  | Setting Terpasang | 767132 |  | 6 A | 0.432 SI | Disabled | - |  | Disabled | -
KPL.25 | GI 150KV DURIKOSAMBI | BUS SECTION#1 150kV | https://docs.google.com/spreadsheets/d/1SsR-gmuvyv848EcuRlQlCCeGH4Cazrq9EmPmc_mTu_A/edit?usp=drive_link |  | Setting Terpasang | 4000/5 A | PHLPTOC1:1 | 1,2xIn | 0,43 | Disabled | - | EFLPTOC1:1 | 0,2xIn | 0,82
KPL.26 | GI 150KV DURIKOSAMBI | BUS SECTION#2 150kV | https://docs.google.com/spreadsheets/d/12NZw8dEE05nopjW6vr5IrGilJeuhtJUOby6n6amqSwQ/edit?usp=drive_link |  | Setting Terpasang | 4000/5 A | PHLPTOC1:1 | 1,2xIn | 0,43 | Disabled | - | EFLPTOC1:1 | 0,2xIn | 0,82
KPL.27 | GI 150KV TANGERANG | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1LuJ0KqViaJukYEU2MkOZpWzbOCoiiGZLJaWPUsP19uk/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1,2 A | 0,48 | - | - |  | DISABLE | DISABLE
KPL.28 | GIS 150KV ALAM SUTERA | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1y7WYbdR2YFqMr8uSMiZyyBSqa2nxm6ST9TM8RrwFBkk/edit?usp=drive_link |  | Setting Terpasang | 4000 / 1 A |  | 1,2 A | 0,285 SI | - | - |  | Disabled | Disabled
KPL.29 | GIS 150KV KEMBANGAN | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1xKaleDAkeqRCk5wwjNohqW3MIaOsXvW2QsIqNm4GOGs/edit?usp=drive_link |  | Setting Terpasang | 4000/5 A |  | 5 | 0.3 | - | - |  | - | -
KPL.30 | GIS 150KV METLAND | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1zMfC4OB6oNMRaOcHSU0mpyNBGId3hHznMHgXra78b88/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1.2A | 0.43 | OFF | OFF |  | BLOCK | BLOCK
KPL.31 | GIS 150KV SUMMARECON GADING SERPONG | KOPEL BUS 150kV | https://docs.google.com/spreadsheets/d/1dAP7lt7vmsuBFUp6ODTKw03RjvHDXILV_EVvkRONEYs/edit?usp=drive_link |  | Setting Terpasang | 767011 |  | 1,2xIn | 0,48 | - | - | Disbale

## SYNCHRO
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GIS | BAY | SIRKIT | RASIO PT | SYNCHRO CHECK | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SYNC | [9 empty] | SYNC
[13 empty] | TAP SET | SETTING | [8 empty] | SET RELAY | SETTING
[14 empty] | DL LB | LL DB | DL DB | Dead Voltage (DV) | Live Voltage (LV) | Vs | Voltage Diff (∆V) | Phase Diff (∆deg) | Freq Diff (∆f) |  | DL LB | LL DB | DL DB | Dead Voltage (DV) | Live Voltage (LV) | Vs | Voltage Diff (∆V) | Phase Diff (∆deg) | Freq Diff (∆f)
PHT.01 | 1 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#1 | #1 | 150 kV/100 V
PHT.02 | 2 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV ANCOL#2 | #2 | 150 kV/100 V
PHT.03 | 3 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#1 | #1 | 150 kV/100 V
PHT.04 | 4 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KARET LAMA#2 | #2 | 150 kV/100 V
PHT.05 | 5 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#1 | #1 | 150 kV/100 V
PHT.06 | 6 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV KETAPANG#2 | #2 | 150 kV/100 V
PHT.07 | 7 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#1 | #1 | 150 kV/100 V
PHT.08 | 8 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV MUARAKARANG LAMA#2 | #2 | 150 kV/100 V
PHT.09 | 9 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#1 | #1 | 150 kV/100 V
PHT.10 | 10 | ULTG ANGKE | GI 150kV ANGKE | PHT 150kV UGC MUARAKARANG LAMA#2 | #2 | 150 kV/100 V
PHT.11 | 11 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#1 | #1 | 150 kV/100 V
PHT.12 | 12 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV LONTAR#2 | #2 | 150 kV/100 V
PHT.13 | 13 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#1 | #1 | 150 kV/100 V
PHT.14 | 14 | ULTG ANGKE | GI 150kV DADAP | PHT 150kV TELUK NAGA#2 | #2 | 150 kV/100 V
PHT.15 | 15 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 150 kV/100 V
PHT.16 | 16 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 150 kV/100 V
PHT.17 | 17 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#1 | #1 | 150 kV/100 V
PHT.18 | 18 | ULTG ANGKE | GI 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA#2 | #2 | 150 kV/100 V
PHT.19 | 19 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#1 | #1 | 150 kV/100 V
PHT.20 | 20 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV ANGKE#2 | #2 | 150 kV/100 V
PHT.21 | 21 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#1 | #1 | 150 kV/100 V
PHT.22 | 22 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN#2 | #2 | 150 kV/100 V
PHT.23 | 23 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#1 | #1 | 150 kV/100 V
PHT.24 | 24 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU#2 | #2 | 150 kV/100 V
PHT.25 | 25 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#1 | #1 | 150 kV/100 V
PHT.26 | 26 | ULTG ANGKE | GI 150kV MUARAKARANG LAMA | PHT 150kV UGC ANGKE#2 | #2 | 150 kV/100 V
PHT.27 | 27 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#1 | #1 | 150 kV/100 V
PHT.28 | 28 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV DURIKOSAMBI#2 | #2 | 150 kV/100 V
PHT.29 | 29 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 150 kV/100 V
PHT.30 | 30 | ULTG ANGKE | GIS 150kV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 150 kV/100 V
PHT.31 | 31 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#1 | #1 | 150 kV/100 V
PHT.32 | 32 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV GROGOL BARU#2 | #2 | 150 kV/100 V
PHT.33 | 33 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#1 | #1 | 150 kV/100 V
PHT.34 | 34 | ULTG ANGKE | GIS 150kV GROGOL | PHT 150kV TOMANG#2 | #2 | 150 kV/100 V
PHT.35 | 35 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#1 | #1 | 150 kV/100 V
PHT.36 | 36 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV DURIKOSAMBI#2 | #2 | 150 kV/100 V
PHT.37 | 37 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#1 | #1 | 150 kV/100 V
PHT.38 | 38 | ULTG ANGKE | GIS 150kV GROGOL BARU | PHT 150kV GROGOL#2 | #2 | 150 kV/100 V
PHT.39 | 39 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#1 | #1 | 150 kV/100 V
PHT.40 | 40 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV DURIKOSAMBI#2 | #2 | 150 kV/100 V
PHT.41 | 41 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#1 | #1 | 150 kV/100 V
PHT.42 | 42 | ULTG ANGKE | GIS 150kV KEBON JERUK | PHT 150kV KARET BARU#2 | #2 | 150 kV/100 V
PHT.43 | 43 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#1 | #1 | 150 kV/100 V
PHT.44 | 44 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV MUARAKARANG BARU#2 | #2 | 150 kV/100 V
PHT.45 | 45 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#1 | #1 | 150 kV/100 V
PHT.46 | 46 | ULTG ANGKE | GIS 150kV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK#2 | #2 | 150 kV/100 V
PHT.47 | 47 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#1 | #1 | 150 kV/100 V
PHT.48 | 48 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV KEMBANGAN#2 | #2 | 150 kV/100 V
PHT.49 | 49 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#1 | #1 | 150 kV/100 V
PHT.50 | 50 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV SENAYAN#2 | #2 | 150 kV/100 V
PHT.51 | 51 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#1 | #1 | 150 kV/100 V
PHT.52 | 52 | ULTG ANGKE | GIS 150kV NEW SENAYAN | PHT 150kV ULUJAMI#2 | #2 | 150 kV/100 V
PHT.53 | 53 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#1 | #1 | 150 kV/100 V
PHT.54 | 54 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT#2 | #2 | 150 kV/100 V
PHT.55 | 55 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#1 | #1 | 150 kV/100 V
PHT.56 | 56 | ULTG ANGKE | GIS 150kV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU#2 | #2 | 150 kV/100 V
PHT.57 | 57 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#1 | #1 | 150 kV/100 V
PHT.58 | 58 | ULTG ANGKE | GIS 150kV TOMANG | PHT 150kV GROGOL#2 | #2 | 150 kV/100 V
PHT.59 | 59 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#1 | #1 | 150 kV/100 V
PHT.60 | 60 | ULTG ANGKE | GIS 150kV ULUJAMI | PHT 150kV NEW SENAYAN#2 | #2 | 150 kV/100 V
PHT.61 | 61 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 500 kV/100 V
PHT.62 | 62 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 500 kV/100 V
PHT.63 | 63 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#1 | #1 | 500 kV/100 V
PHT.64 | 64 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV DURIKOSAMBI#2 | #2 | 500 kV/100 V
PHT.65 | 65 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 | 500 kV/100 V
PHT.66 | 66 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 | 500 kV/100 V
PHT.67 | 67 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#1 | #1 | 500 kV/100 V
PHT.68 | 68 | ULTG ANGKE | GISTET 500kV MUARAKARANG BARU | PHT 500kV TANJUNG PRIOK#2 | #2 | 500 kV/100 V
PHT.69 | 69 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#1 | #1 | 150 kV/100 V
PHT.70 | 70 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV CIKUPA#2 | #2 | 150 kV/100 V
PHT.71 | 71 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 150 kV/100 V
PHT.72 | 72 | ULTG CITRA RAYA | GI 150kV CURUG | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 150 kV/100 V
PHT.73 | 73 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS | #1 | 150 kV/100 V
PHT.74 | 74 | ULTG CITRA RAYA | GI 150kV GAJAH TUNGGAL | PHT 150kV PASAR KEMIS BARU | #1 | 150 kV/100 V
PHT.75 | 75 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV TANGERANG BARU | #1 | 150 kV/100 V
PHT.76 | 76 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV CENGKARENG BARU | #1 | 150 kV/100 V
PHT.77 | 77 | ULTG CITRA RAYA | GI 150kV ITS | PHT 150kV KONSUMEN | #1 | 150 kV/100 V
PHT.78 | 78 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#1 | #1 | 150 kV/100 V
PHT.79 | 79 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV CIKUPA#2 | #2 | 150 kV/100 V
PHT.80 | 80 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#1 | #1 | 150 kV/100 V
PHT.81 | 81 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV JATAKE BARU#2 | #2 | 150 kV/100 V
PHT.82 | 82 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 150 kV/100 V
PHT.83 | 83 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 150 kV/100 V
PHT.84 | 84 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#1 | #1 | 150 kV/100 V
PHT.85 | 85 | ULTG CITRA RAYA | GI 150kV JATAKE | PHT 150kV MAXIMANGANDO#2 | #2 | 150 kV/100 V
PHT.86 | 86 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 150 kV/100 V
PHT.87 | 87 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 150 kV/100 V
PHT.88 | 88 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#1 | #1 | 150 kV/100 V
PHT.89 | 89 | ULTG CITRA RAYA | GI 150kV MAXIMANGANDO | PHT 150kV JATAKE#2 | #2 | 150 kV/100 V
PHT.90 | 90 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#1 | #1 | 150 kV/100 V
PHT.91 | 91 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV BALARAJA#2 | #2 | 150 kV/100 V
PHT.92 | 92 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#1 | #1 | 150 kV/100 V
PHT.93 | 93 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV LONTAR#2 | #2 | 150 kV/100 V
PHT.94 | 94 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#1 | #1 | 150 kV/100 V
PHT.95 | 95 | ULTG CITRA RAYA | GI 150kV SINDANG JAYA | PHT 150kV SUVARNA SUTERA#2 | #2 | 150 kV/100 V
PHT.96 | 96 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#1 | #1 | 150 kV/100 V
PHT.97 | 97 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV LONTAR#2 | #2 | 150 kV/100 V
PHT.98 | 98 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV ITS | #1 | 150 kV/100 V
PHT.99 | 99 | ULTG CITRA RAYA | GI 150kV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 | 150 kV/100 V
PHT.100 | 100 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#1 | #1 | 150 kV/100 V
PHT.101 | 101 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV DADAP#2 | #2 | 150 kV/100 V
PHT.102 | 102 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#1 | #1 | 150 kV/100 V
PHT.103 | 103 | ULTG CITRA RAYA | GI 150kV TELUK NAGA | PHT 150kV SEPATAN#2 | #2 | 150 kV/100 V
PHT.104 | 104 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#1 | #1 | 150 kV/100 V
PHT.105 | 105 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV JATAKE#2 | #2 | 150 kV/100 V
PHT.106 | 106 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#1 | #1 | 150 kV/100 V
PHT.107 | 107 | ULTG CITRA RAYA | GIS 150kV JATAKE BARU | PHT 150kV TANGERANG#2 | #2 | 150 kV/100 V
PHT.108 | 108 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#1 | #1 | 150 kV/100 V
PHT.109 | 109 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV SINDANG JAYA#2 | #2 | 150 kV/100 V
PHT.110 | 110 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#1 | #1 | 150 kV/100 V
PHT.111 | 111 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV DADAP#2 | #2 | 150 kV/100 V
PHT.112 | 112 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#1 | #1 | 150 kV/100 V
PHT.113 | 113 | ULTG CITRA RAYA | GIS 150kV LONTAR | PHT 150kV TANGERANG BARU#2 | #2 | 150 kV/100 V
PHT.114 | 114 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#1 | #1 | 150 kV/100 V
PHT.115 | 115 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV DURIKOSAMBI#2 | #2 | 150 kV/100 V
PHT.116 | 116 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#1 | #1 | 150 kV/100 V
PHT.117 | 117 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV CENGKARENG BARU#2 | #2 | 150 kV/100 V
PHT.118 | 118 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#1 | #1 | 150 kV/100 V
PHT.119 | 119 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG | PHT 150kV TANGERANG#2 | #2 | 150 kV/100 V
PHT.120 | 120 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#1 | #1 | 150 kV/100 V
PHT.121 | 121 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV BANDARA SOEKARNO HATTA#2 | #2 | 150 kV/100 V
PHT.122 | 122 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#1 | #1 | 150 kV/100 V
PHT.123 | 123 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV CENGKARENG#2 | #2 | 150 kV/100 V
PHT.124 | 124 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV ITS | #1 | 150 kV/100 V
PHT.125 | 125 | ULTG DURIKOSAMBI | GI 150kV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 | 150 kV/100 V
PHT.126 | 126 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#1 | #1 | 150 kV/100 V
PHT.127 | 127 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV ALAM SUTERA#2 | #2 | 150 kV/100 V
PHT.128 | 128 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#1 | #1 | 150 kV/100 V
PHT.129 | 129 | ULTG DURIKOSAMBI | GI 150kV CILEDUG | PHT 150kV METLAND#2 | #2 | 150 kV/100 V
PHT.130 | 130 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#1 | #1 | 150 kV/100 V
PHT.131 | 131 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV CENGKARENG#2 | #2 | 150 kV/100 V
PHT.132 | 132 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV LMK | #1 | 150 kV/100 V
PHT.133 | 133 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#1 | #1 | 150 kV/100 V
PHT.134 | 134 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV GROGOL BARU#2 | #2 | 150 kV/100 V
PHT.135 | 135 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#1 | #1 | 150 kV/100 V
PHT.136 | 136 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEBON JERUK#2 | #2 | 150 kV/100 V
PHT.137 | 137 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#1 | #1 | 150 kV/100 V
PHT.138 | 138 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV KEMBANGAN#2 | #2 | 150 kV/100 V
PHT.139 | 139 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#1 | #1 | 150 kV/100 V
PHT.140 | 140 | ULTG DURIKOSAMBI | GI 150kV DURIKOSAMBI | PHT 150kV DAAN MOGOT#2 | #2 | 150 kV/100 V
PHT.141 | 141 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#1 | #1 | 150 kV/100 V
PHT.142 | 142 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV CENGKARENG#2 | #2 | 150 kV/100 V
PHT.143 | 143 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#1 | #1 | 150 kV/100 V
PHT.144 | 144 | ULTG DURIKOSAMBI | GI 150kV TANGERANG | PHT 150kV JATAKE BARU#2 | #2 | 150 kV/100 V
PHT.145 | 145 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#1 | #1 | 150 kV/100 V
PHT.146 | 146 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV CILEDUG#2 | #2 | 150 kV/100 V
PHT.147 | 147 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#1 | #1 | 150 kV/100 V
PHT.148 | 148 | ULTG DURIKOSAMBI | GIS 150kV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG#2 | #2 | 150 kV/100 V
PHT.149 | 149 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#1 | #1 | 150 kV/100 V
PHT.150 | 150 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV METLAND#2 | #2 | 150 kV/100 V
PHT.151 | 151 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#1 | #1 | 150 kV/100 V
PHT.152 | 152 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV DURIKOSAMBI#2 | #2 | 150 kV/100 V
PHT.153 | 153 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#1 | #1 | 150 kV/100 V
PHT.154 | 154 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV NEW SENAYAN#2 | #2 | 150 kV/100 V
PHT.155 | 155 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#1 | #1 | 150 kV/100 V
PHT.156 | 156 | ULTG DURIKOSAMBI | GIS 150kV KEMBANGAN | PHT 150kV PETUKANGAN#2 | #2 | 150 kV/100 V
PHT.157 | 157 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#1 | #1 | 150 kV/100 V
PHT.158 | 158 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV KEMBANGAN#2 | #2 | 150 kV/100 V
PHT.159 | 159 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#1 | #1 | 150 kV/100 V
PHT.160 | 160 | ULTG DURIKOSAMBI | GIS 150kV METLAND | PHT 150kV CILEDUG#2 | #2 | 150 kV/100 V
PHT.161 | 161 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#1 | #1 | 150 kV/100 V
PHT.162 | 162 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA#2 | #2 | 150 kV/100 V
PHT.163 | 163 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#1 | #1 | 150 kV/100 V
PHT.164 | 164 | ULTG DURIKOSAMBI | GIS 150kV SUMMARECON GADING SERPONG | PHT 150kV CURUG#2 | #2 | 150 kV/100 V
PHT.165 | 165 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 500 kV/100 V
PHT.166 | 166 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 500 kV/100 V
PHT.167 | 167 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 500 kV/100 V
PHT.168 | 168 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 500 kV/100 V
PHT.169 | 169 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV GANDUL#1 | #1 | 500 kV/100 V
PHT.170 | 170 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV KEMBANGAN#2 | #2 | 500 kV/100 V
PHT.171 | 171 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#1 | #1 | 500 kV/100 V
PHT.172 | 172 | ULTG DURIKOSAMBI | GISTET 500kV DURIKOSAMBI | PHT 500kV MUARAKARANG#2 | #2 | 500 kV/100 V
PHT.173 | 173 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 500 kV/100 V
PHT.174 | 174 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 500 kV/100 V
PHT.175 | 175 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 500 kV/100 V
PHT.176 | 176 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 500 kV/100 V
PHT.177 | 177 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 500 kV/100 V
PHT.178 | 178 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 500 kV/100 V
PHT.179 | 179 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#1 | #1 | 500 kV/100 V
PHT.180 | 180 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV DURIKOSAMBI#2 | #2 | 500 kV/100 V
PHT.181 | 181 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#1 | #1 | 500 kV/100 V
PHT.182 | 182 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV BALARAJA#2 | #2 | 500 kV/100 V
PHT.183 | 183 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#1 | #1 | 500 kV/100 V
PHT.184 | 184 | ULTG DURIKOSAMBI | GISTET 500kV KEMBANGAN | PHT 500kV GANDUL#2 | #2 | 500 kV/100 V

## SYNCHROx (hidden)
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
NO | GI / GIS | BAY | BAY | ULTG | GI / GIS | BAY | SIRKIT | PT BUS | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SETTING
[14 empty] | DL LB | LL DB | DL DB | Dead Voltage (DV) | Live Voltage (LV) | Voltage Diff (∆V) | Phase Diff (∆deg) | Freq Diff (∆f)
97 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0011 - PHT 150kV MUARAKARANG LAMA #1 | PHT 150kV MUARAKARANG LAMA #1 | ULTG ANGKE | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA | #1
98 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0012 - PHT 150kV MUARAKARANG LAMA #2 | PHT 150kV MUARAKARANG LAMA #2 | ULTG ANGKE | GI 150KV MUARAKARANG BARU | PHT 150kV MUARAKARANG LAMA | #2
99 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0022 - PHT 150kV PANTAI INDAH KAPUK #1 | PHT 150kV PANTAI INDAH KAPUK #1 | ULTG ANGKE | GI 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK | #1
100 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0013 - PHT 150kV PANTAI INDAH KAPUK #2 | PHT 150kV PANTAI INDAH KAPUK #2 | ULTG ANGKE | GI 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK | #2
101 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0045 - PHT 150kV ANGKE #1 | PHT 150kV ANGKE #1 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE | #1 | 150 kV / 100 V | Siemens |  |  | Numerik |  | Aktif | Aktif | Aktif | < 12 | > 52 | 5.7 | 20 | 0.17
102 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0046 - PHT 150kV ANGKE #2 | PHT 150kV ANGKE #2 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE | #2 | 150 kV / 100 V | Siemens |  |  | Numerik |  | Aktif | Aktif | Aktif | < 12 | > 52 | 5.7 | 20 | 0.17
105 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0035 - PHT 150kV BUDIKEMULYAN #1 | PHT 150kV BUDIKEMULYAN #1 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN | #1
106 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0040 - PHT 150kV BUDIKEMULYAN #2 | PHT 150kV BUDIKEMULYAN #2 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN | #2
107 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0034 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV DURIKOSAMBI | #1
108 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0039 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV DURIKOSAMBI | #2
109 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0041 - PHT 150kV MUARAKARANG BARU #1 | PHT 150kV MUARAKARANG BARU #1 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU | #1
110 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0042 - PHT 150kV MUARAKARANG BARU #2 | PHT 150kV MUARAKARANG BARU #2 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU | #2
103 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-DUM.000-B0084 - PHT 150kV UGC ANGKE #1 | PHT 150kV UGC ANGKE #1 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE | #1
104 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-DUM.000-B0085 - PHT 150kV UGC ANGKE #2 | PHT 150kV UGC ANGKE #2 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE | #2
161 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0005 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG ANGKE | GIS 150KV DAAN MOGOT | KOPEL BUS
157 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0003 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | ULTG ANGKE | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI | #1 | 150 kV / 100 V |  |  |  | Numerik | 2020
158 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0004 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | ULTG ANGKE | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI | #2 | 150 kV / 100 V | ABB | REL 670 | T1645101 | Numerik | 2020 | aktif | aktif | aktif |  |  | 0.15 | 25 | 0.167
159 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0001 - PHT 150kV PANTAI INDAH KAPUK #1 | PHT 150kV PANTAI INDAH KAPUK #1 | ULTG ANGKE | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK | #1 |  |  |  |  | Numerik | 2020
160 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0002 - PHT 150kV PANTAI INDAH KAPUK #2 | PHT 150kV PANTAI INDAH KAPUK #2 | ULTG ANGKE | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK | #2 |  |  |  |  | Numerik | 2020
164 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0011 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG ANGKE | GIS 150KV GROGOL | KOPEL BUS |  | 150 kV / 100 V | Alsthom | MAVS | 422875L | Elektromekanik |  | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 15 | 0.17
162 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0004 - PHT 150kV GROGOL BARU #1 | PHT 150kV GROGOL BARU #1 | ULTG ANGKE | GIS 150KV GROGOL | PHT 150kV GROGOL BARU | #1 | 150 kV / 100 V | Alsthom | LFAA 101 | 422875L | Elektromekanik |  | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 15 | 0.17
163 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0005 - PHT 150kV GROGOL BARU #2 | PHT 150kV GROGOL BARU #2 | ULTG ANGKE | GIS 150KV GROGOL | PHT 150kV GROGOL BARU | #2 | 150 kV / 100 V | Alsthom | LFAA 101 | 422717L | Elektromekanik |  | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 15 | 0.17
169 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0005 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG ANGKE | GIS 150KV GROGOL BARU | KOPEL BUS
165 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0003 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | ULTG ANGKE | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI | #1 | 150 kV / 100 V | [5 empty] | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 15 | 0.17
166 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0004 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | ULTG ANGKE | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI | #2 | 150 kV / 100 V | Alsthom | MAVS | 422875L | Elektromekanik |  | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 15 | 0.17
167 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0001 - PHT 150kV GROGOL #1 | PHT 150kV GROGOL #1 | ULTG ANGKE | GIS 150KV GROGOL BARU | PHT 150kV GROGOL | #1
168 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0002 - PHT 150kV GROGOL #2 | PHT 150kV GROGOL #2 | ULTG ANGKE | GIS 150KV GROGOL BARU | PHT 150kV GROGOL | #2
179 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0010 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG ANGKE | GIS 150KV KEBON JERUK | KOPEL BUS
175 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0007 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | ULTG ANGKE | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI | #1
176 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0008 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | ULTG ANGKE | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI | #2
177 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0006 - PHT 150kV KARET BARU #1 | PHT 150kV KARET BARU #1 | ULTG ANGKE | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU | #1
178 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0011 - PHT 150kV KARET BARU #2 | PHT 150kV KARET BARU #2 | ULTG ANGKE | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU | #2
199 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0006 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG ANGKE | GIS 150KV NEW SENAYAN | KOPEL BUS
195 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0007 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | ULTG ANGKE | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN | #1
196 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0005 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | ULTG ANGKE | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN | #2
197 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-DUM.000-B0039 - PHT 150kV SENAYAN #1 | PHT 150kV SENAYAN #1 | ULTG ANGKE | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN | #1
198 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-DUM.000-B0040 - PHT 150kV SENAYAN #2 | PHT 150kV SENAYAN #2 | ULTG ANGKE | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN | #2
204 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-BO11 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | KOPEL BUS
200 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0003 - PHT 150kV DAAN MOGOT #1 | PHT 150kV DAAN MOGOT #1 | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT | #1
201 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0004 - PHT 150kV DAAN MOGOT #2 | PHT 150kV DAAN MOGOT #2 | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT | #2
202 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | #N/A | PHT 150kV GIS MUARAKARANG BARU #1 | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV GIS MUARAKARANG BARU | #1 | 150 kV / 100 V | Alstom | MiCom P545 | 197931U | Numerik |  | aktif | aktif | tdk aktif | 11.5 | 52 | 6 | 15 | 0.167
203 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0002 - PHT 150kV MUARAKARANG BARU #2 | PHT 150kV MUARAKARANG BARU #2 | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV MUARAKARANG BARU | #2
222 |  |  |  | ULTG ANGKE | GIS 150KV TOMANG | KOPEL BUS |  | 150 kV / 100 V | Schneider | MiCom C264 |  | Numerik | 2021 | aktif | aktif | aktif | < 11,5 | > 52 | 6 V | 15 | 0.167
220 |  |  |  | ULTG ANGKE | GIS 150KV TOMANG | PHT 150kV GROGOL | #1 | 150 kV / 100 V | Schneider | MiCom C264 |  | Numerik | 2021 | aktif | aktif | aktif | < 11,5 | > 52 | 6 V | 15 | 0.167
221 |  |  |  | ULTG ANGKE | GIS 150KV TOMANG | PHT 150kV GROGOL | #2 | 150 kV / 100 V | Schneider | MiCom C264 |  | Numerik | 2021 | aktif | aktif | aktif | < 11,5 | > 52 | 6 V | 15 | 0.167
225 |  |  |  | ULTG ANGKE | GIS 150KV ULUJAMI | KOPEL BUS
223 |  |  |  | ULTG ANGKE | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN | #1
224 |  |  |  | ULTG ANGKE | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN | #2
56 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0006 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG CITRA RAYA | GI 150KV CURUG | KOPEL BUS
52 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0008 - PHT 150kV CIKUPA #1 | PHT 150kV CIKUPA #1 | ULTG CITRA RAYA | GI 150KV CURUG | PHT 150kV CIKUPA | #1
53 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-DUM.000-B0012 - PHT 150kV CIKUPA #2 | PHT 150kV CIKUPA #2 | ULTG CITRA RAYA | GI 150KV CURUG | PHT 150kV CIKUPA | #2 | 150 kV / 100 V | GEC Alsthom | MAVS | 001719J | Elektromekanik |  | aktif | aktif | tdk aktif | <21 | >52 | 52 | 15 | 0.17
54 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0003 - PHT 150kV SUMMARECON GADING SERPONG #1 | PHT 150kV SUMMARECON GADING SERPONG #1 | ULTG CITRA RAYA | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG | #1 | 150 kV / 100 V | GEC Alsthom | MAVS | 001722J | Elektromekanik |  | aktif | aktif
55 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-DUM.000-B0013 - PHT 150kV SUMMARECON GADING SERPONG #2 | PHT 150kV SUMMARECON GADING SERPONG #2 | ULTG CITRA RAYA | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG | #2 | 150 kV / 100 V | Alstom | MiCom P545 | 34721255/02/19 | Numerik |  | aktif | aktif | tdk aktif | <11,5 | >52 | 6 | 15 | 0.165
82 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0003 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG CITRA RAYA | GI 150KV JATAKE | KOPEL BUS
76 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0010 - PHT 150kV CIKUPA #1 | PHT 150kV CIKUPA #1 | ULTG CITRA RAYA | GI 150KV JATAKE | PHT 150kV CIKUPA | #1 | 150 kV / 100 V | ABB | RXNAA4 | 8839
77 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0009 - PHT 150kV CIKUPA #2 | PHT 150kV CIKUPA #2 | ULTG CITRA RAYA | GI 150KV JATAKE | PHT 150kV CIKUPA | #2 | 150 kV / 100 V | ABB | RXNAA4 | 8839
80 | TRS-3413-055.055 - GI 150kV JATAKE | #N/A | PHT 150kV JATAKE BARU #1 | ULTG CITRA RAYA | GI 150KV JATAKE | PHT 150kV JATAKE BARU | #1 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021 | aktif | aktif
81 | TRS-3413-055.055 - GI 150kV JATAKE | #N/A | PHT 150kV JATAKE BARU #2 | ULTG CITRA RAYA | GI 150KV JATAKE | PHT 150kV JATAKE BARU | #2 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021 | aktif | aktif
78 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0013 - PHT 150kV MAXIMANGANDO #1 | PHT 150kV MAXIMANGANDO #1 | ULTG CITRA RAYA | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO | #1
79 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0014 - PHT 150kV MAXIMANGANDO #2 | PHT 150kV MAXIMANGANDO #2 | ULTG CITRA RAYA | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO | #2 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik |  | aktif | aktif | tdk aktif | < 10,96 | > 51,9 | 5.7 | 15 | 0,17 Hz
91 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0011 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG CITRA RAYA | GI 150KV MAXIMANGANDO | KOPEL BUS
89 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0006 - PHT 150kV JATAKE #1 | PHT 150kV JATAKE #1 | ULTG CITRA RAYA | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE | #1
90 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0007 - PHT 150kV JATAKE #2 | PHT 150kV JATAKE #2 | ULTG CITRA RAYA | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE | #2
133 | - GI 150kV SINDANG JAYA | #N/A | KOPEL BUS 150kV | ULTG CITRA RAYA | GI 150KV SINDANG JAYA | KOPEL BUS
131 | - GI 150kV SINDANG JAYA | #N/A | PHT 150kV LONTAR #1 | ULTG CITRA RAYA | GI 150KV SINDANG JAYA | PHT 150kV LONTAR | #1 | 150 kV / 100 V | NR |  |  | Numerik | 2021
132 | - GI 150kV SINDANG JAYA | #N/A | PHT 150kV LONTAR #2 | ULTG CITRA RAYA | GI 150KV SINDANG JAYA | PHT 150kV LONTAR | #2 | 150 kV / 100 V | NR |  |  | Numerik | 2021
143 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0012 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | KOPEL BUS
140 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | #N/A | PHT 150kV CENGKARENG BARU | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU |  | 150 kV / 100 V | Areva | KAVR 13 | 3354776/02/09 | Elektromekanik |  | aktif | aktif | aktif | <11,5 | >52 | 6 | 15 | 0.16
139 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | #N/A | PHT 150kV ITS | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | PHT 150kV ITS |  | 150 kV / 100 V | Areva | KAVR 13 | 3357108/02/09 | Elektromekanik |  | aktif | aktif | aktif | <17,25 | >78 | 6 / 9 | 15 | 0.167
141 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0001 - PHT 150kV LONTAR #1 | PHT 150kV LONTAR #1 | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | PHT 150kV LONTAR | #1 | 150 kV / 100 V | Areva | KAVR 13 | 3354779/02/09 | Elektromekanik
142 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0013 - PHT 150kV LONTAR #2 | PHT 150kV LONTAR #2 | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | PHT 150kV LONTAR | #2 | 150 kV / 100 V | Areva | KAVR 13 | 3354778/02/09 | Elektromekanik
148 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0004 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG CITRA RAYA | GI 150KV TELUK NAGA | KOPEL BUS
144 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0010 - PHT 150kV LONTAR #1 | PHT 150kV LONTAR #1 | ULTG CITRA RAYA | GI 150KV TELUK NAGA | PHT 150kV LONTAR | #1 | 150 kV / 100 V | Areva | KAVR 13 | 3354784/02/09 | Elektromekanik
145 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0011 - PHT 150kV LONTAR #2 | PHT 150kV LONTAR #2 | ULTG CITRA RAYA | GI 150KV TELUK NAGA | PHT 150kV LONTAR | #2 | 150 kV / 100 V | Areva | KAVR 13 | 3354775/02/09 | Elektromekanik
146 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0009 - PHT 150kV SEPATAN #1 | PHT 150kV SEPATAN #1 | ULTG CITRA RAYA | GI 150KV TELUK NAGA | PHT 150kV SEPATAN | #1 | 150 kV / 100 V | Alsthom | MAVS 01 | 689635F | Elektromekanik |  | aktif | aktif | - | - | - | - | 15 | -
147 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0001 - PHT 150kV SEPATAN #2 | PHT 150kV SEPATAN #2 | ULTG CITRA RAYA | GI 150KV TELUK NAGA | PHT 150kV SEPATAN | #2 | 150 kV / 100 V | Alsthom | MAVS 01 | 690087F | Elektromekanik
174 | - GIS 150kV JATAKE BARU | #N/A | KOPEL BUS 150kV | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | KOPEL BUS
170 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV JATAKE #1 | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | PHT 150kV JATAKE | #1 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021
171 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV JATAKE #2 | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | PHT 150kV JATAKE | #2 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021
172 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV TANGERANG #1 | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG | #1 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021
173 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV TANGERANG #2 | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG | #2 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021
189 | TRS-3413-144.144 - GIS 150kV LONTAR | #N/A | PHT 150kV SINDANG JAYA #1 | ULTG CITRA RAYA | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA | #1 | 150 kV / 100 V | Schneider | MiCom P443 |  | Numerik
190 | TRS-3413-144.144 - GIS 150kV LONTAR | #N/A | PHT 150kV SINDANG JAYA #2 | ULTG CITRA RAYA | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA | #2 | 150 kV / 100 V | Schneider | MiCom P443 |  | Numerik
193 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0014 - PHT 150kV TANGERANG BARU #1 | PHT 150kV TANGERANG BARU #1 | ULTG CITRA RAYA | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU | #1 | 150 kV / 100 V | NR | RCS-902 | 7842101100401 | Numerik
194 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0016 - PHT 150kV TANGERANG BARU #2 | PHT 150kV TANGERANG BARU #2 | ULTG CITRA RAYA | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU | #2 | 150 kV / 100 V | NR | RCS-902 | 7842101100501 | Numerik
191 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0013 - PHT 150kV TELUK NAGA #1 | PHT 150kV TELUK NAGA #1 | ULTG CITRA RAYA | GIS 150KV LONTAR | PHT 150kV TELUK NAGA | #1 | 150 kV / 100 V | NR | RCS-902 | 7842101100601 | Numerik
192 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0022 - PHT 150kV TELUK NAGA #2 | PHT 150kV TELUK NAGA #2 | ULTG CITRA RAYA | GIS 150KV LONTAR | PHT 150kV TELUK NAGA | #2 | 150 kV / 100 V | NR | RCS-902 | 7842101100301 | Numerik
11 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0003 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | KOPEL BUS |  | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
1 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0005 - PHT 150kV ANCOL #1 | PHT 150kV ANCOL #1 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV ANCOL | #1
2 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0002 - PHT 150kV ANCOL #2 | PHT 150kV ANCOL #2 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV ANCOL | #2
3 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0012 - PHT 150kV KARET LAMA #1 | PHT 150kV KARET LAMA #1 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KARET LAMA | #1
4 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0013 - PHT 150kV KARET LAMA #2 | PHT 150kV KARET LAMA #2 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KARET LAMA | #2 | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
5 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0001 - PHT 150kV KETAPANG #1 | PHT 150kV KETAPANG #1 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KETAPANG | #1 | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
6 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0004 - PHT 150kV KETAPANG #2 | PHT 150kV KETAPANG #2 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KETAPANG | #2 | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
7 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0014 - PHT 150kV MUARAKARANG LAMA #1 | PHT 150kV MUARAKARANG LAMA #1 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA | #1 | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
8 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0015 - PHT 150kV MUARAKARANG LAMA #2 | PHT 150kV MUARAKARANG LAMA #2 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA | #2 | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
9 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-DUM.000-B0008 - PHT 150kV UGC MUARAKARANG LAMA #1 | PHT 150kV UGC MUARAKARANG LAMA #1 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA | #1 | 150 kV / 100 V | [5 empty] | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
10 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-DUM.000-B0009 - PHT 150kV UGC MUARAKARANG LAMA #2 | PHT 150kV UGC MUARAKARANG LAMA #2 | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA | #2 | 150 kV / 100 V |  | MiCom C264 | 34442452/05/18 | Numerik |  | aktif | aktif | tdk aktif | < 12 | > 52 | 6 | 15
25 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0005 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | KOPEL BUS |  | 150 kV / 100 V |  | KAVS 100 | 3355332/02/09
23 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0017 - PHT 150kV CENGKARENG BARU #1 | PHT 150kV CENGKARENG BARU #1 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU | #1 | 150 kV / 100 V | GEC Alsthom | MiCom P545 | 33980376/02/17 | Numerik |  | aktif | aktif | tdk aktif | <11,5 | >52 | 7 | 15 | 0.165
24 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0018 - PHT 150kV CENGKARENG BARU #2 | PHT 150kV CENGKARENG BARU #2 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU | #2 | 150 kV / 100 V | GEC Alsthom | MiCom P545 | 33980375/02/17 | Numerik |  | aktif | aktif | tdk aktif | <11,5 | >52 | 7 | 15 | 0.165
19 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0013 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI | #1
20 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0014 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI | #2
21 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0016 - PHT 150kV TANGERANG #1 | PHT 150kV TANGERANG #1 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | PHT 150kV TANGERANG | #1
22 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0015 - PHT 150kV TANGERANG #2 | PHT 150kV TANGERANG #2 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | PHT 150kV TANGERANG | #2
30 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0003 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | KOPEL BUS
26 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0006 - PHT 150kV CENGKARENG #1 | PHT 150kV CENGKARENG #1 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG | #1
27 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0007 - PHT 150kV CENGKARENG #2 | PHT 150kV CENGKARENG #2 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG | #2
29 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | #N/A | PHT 150kV ITS | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | PHT 150kV ITS
28 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | #N/A | PHT 150kV TANGERANG BARU | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU |  | 150 kV / 100 V | Alstom | MiCom P545 | 33980371/02/17 | Numerik |  | aktif | aktif | tdk aktif | <11,5 | >52 | 6.5 | 15 | 0.165
44 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0003 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GI 150KV CILEDUG | KOPEL BUS
40 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0001 - PHT 150kV ALAM SUTERA #1 | PHT 150kV ALAM SUTERA #1 | ULTG DURIKOSAMBI | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA | #1 | 150 kV / 100 V | Alsthom | MAVS | 17909 | Elektromekanik |  | aktif | aktif
41 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0017 - PHT 150kV ALAM SUTERA #2 | PHT 150kV ALAM SUTERA #2 | ULTG DURIKOSAMBI | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA | #2 | 150 kV / 100 V | Alstom | MiCom P545 | 34665003/12/18 | Numerik
42 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0004 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | ULTG DURIKOSAMBI | GI 150KV CILEDUG | PHT 150kV KEMBANGAN | #1 | [6 empty] | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 20 | 0.17
43 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0016 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | ULTG DURIKOSAMBI | GI 150KV CILEDUG | PHT 150kV KEMBANGAN | #2 | 150 kV / 100 V | Alstom | MiCom P545 | 34721257/02/19 | Numerik |  | aktif | aktif | aktif | 2021-05-11 | 52 | 6 | 15 | 0,1675 Hz
74 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0028 - BUS SECTION A 150kV | BUS SECTION A 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | BUS SECTION | A
75 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0029 - BUS SECTION B 150kV | BUS SECTION B 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | BUS SECTION | B
72 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0013 - KOPEL BUS #1 150kV | KOPEL BUS #1 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | KOPEL BUS | #1
73 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0014 - KOPEL BUS #2 150kV | KOPEL BUS #2 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | KOPEL BUS | #2
57 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0023 - PHT 150kV CENGKARENG #1 | PHT 150kV CENGKARENG #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG | #1 | 150 kV / 100 V | GEC Alsthom | MAVS | 588664C | Elektromekanik
58 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0022 - PHT 150kV CENGKARENG #2 | PHT 150kV CENGKARENG #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG | #2 | 150 kV / 100 V | GEC Alsthom | MAVS | 588663C | Elektromekanik
68 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0038 - PHT 150kV DAAN MOGOT #1 | PHT 150kV DAAN MOGOT #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT | #1
69 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0039 - PHT 150kV DAAN MOGOT #2 | PHT 150kV DAAN MOGOT #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT | #2
59 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0008 - PHT 150kV GROGOL BARU #1 | PHT 150kV GROGOL BARU #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU | #1 | 150 kV / 100 V | GEC Alsthom | MAVS | 588664C | Elektromekanik |  | aktif | aktif
60 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0009 - PHT 150kV GROGOL BARU #2 | PHT 150kV GROGOL BARU #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU | #2 | 150 kV / 100 V | GEC Alsthom | MAVS | 250855L | Elektromekanik |  | aktif | aktif | tdk aktif | <12 | >52 | 5.7 | 15 | 0.17
61 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0021 - PHT 150kV KEBON JERUK #1 | PHT 150kV KEBON JERUK #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK | #1
62 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0004 - PHT 150kV KEBON JERUK #2 | PHT 150kV KEBON JERUK #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK | #2
63 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0026 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN | #1
64 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0027 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN | #2
65 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0006 - PHT 150kV LMK | PHT 150kV LMK | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV LMK |  | 150 kV / 100 V | Alsthom | MAVS | 620479F | Elektromekanik
66 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0018 - PHT 150kV MUARAKARANG LAMA #1 | PHT 150kV MUARAKARANG LAMA #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV MUARAKARANG LAMA | #1 | 150 kV / 100 V | Alsthom | MAVS | 588662C | Elektromekanik
67 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0003 - PHT 150kV MUARAKARANG LAMA #2 | PHT 150kV MUARAKARANG LAMA #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV MUARAKARANG LAMA | #2 | 150 kV / 100 V | Alsthom | MAVS | 588661C | Elektromekanik
70 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0030 - PHT 150kV PETUKANGAN #1 | PHT 150kV PETUKANGAN #1 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV PETUKANGAN | #1 | 150 kV / 100 V | Alsthom | MAVS | 588659C | Elektromekanik
71 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0017 - PHT 150kV PETUKANGAN #2 | PHT 150kV PETUKANGAN #2 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV PETUKANGAN | #2 | 150 kV / 100 V | Alsthom | MAVS | 588660C | Elektromekanik
138 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0006 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GI 150KV TANGERANG | KOPEL BUS
134 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0013 - PHT 150kV CENGKARENG #1 | PHT 150kV CENGKARENG #1 | ULTG DURIKOSAMBI | GI 150KV TANGERANG | PHT 150kV CENGKARENG | #1 | 150 kV / 100 V | Siemens | 7SL87 | P1C289087 | Numerik |  | aktif | aktif | tdk aktif | 5 | 52 | 5 | 15 | 0.17
135 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0014 - PHT 150kV CENGKARENG #2 | PHT 150kV CENGKARENG #2 | ULTG DURIKOSAMBI | GI 150KV TANGERANG | PHT 150kV CENGKARENG | #2 | 150 kV / 100 V | GEC | MAVS 02 | 603972C | Elektromekanik
136 | TRS-3413-057.057 - GI 150kV TANGERANG | #N/A | PHT 150kV JATAKE BARU #1 | ULTG DURIKOSAMBI | GI 150KV TANGERANG | PHT 150kV JATAKE BARU | #1 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021 | aktif | aktif
137 | TRS-3413-057.057 - GI 150kV TANGERANG | #N/A | PHT 150kV JATAKE BARU #2 | ULTG DURIKOSAMBI | GI 150KV TANGERANG | PHT 150kV JATAKE BARU | #2 | 150 kV / 100 V | NR | PCS-9705 |  | Numerik | 2021 | aktif | aktif
156 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0011 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | KOPEL BUS |  | 150 kV / 100 V | Alstom | KAVS 100 | 3206337/02/12 |  |  | aktif | aktif | aktif | <7,5 | >52,5 | 5.25 | 15 | 0.167
152 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0007 - PHT 150kV CILEDUG #1 | PHT 150kV CILEDUG #1 | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG | #1 | 150 kV / 100 V | Alstom | MiCom P841 | 32066107/02/12 | Numerik | 2014 | aktif | aktif
153 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0012 - PHT 150kV CILEDUG #2 | PHT 150kV CILEDUG #2 | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG | #2 | 150 kV / 100 V | Alstom | MiCom P841 | 32068105/02/12 | Numerik | 2014
154 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0013 - PHT 150kV SUMMARECON GADING SERPONG #1 | PHT 150kV SUMMARECON GADING SERPONG #1 | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG | #1 | 150 kV / 100 V | ABB | RED 670 | T1809136 | Numerik | 2019
155 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-DUM.000-B0020 - PHT 150kV SUMMARECON GADING SERPONG #2 | PHT 150kV SUMMARECON GADING SERPONG #2 | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG | #2 | 150 kV / 100 V | ABB | RED 670 | T1809137 | Numerik | 2019 | aktif | aktif
188 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0014 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | KOPEL BUS
180 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0002 - PHT 150kV CILEDUG #1 | PHT 150kV CILEDUG #1 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV CILEDUG | #1
181 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0005 - PHT 150kV CILEDUG #2 | PHT 150kV CILEDUG #2 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV CILEDUG | #2
182 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0006 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI | #1
183 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0007 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI | #2
184 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | #N/A | PHT 150kV NEW PHT 150kV SENAYAN #1 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV NEW PHT 150kV SENAYAN | #1
185 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | #N/A | PHT 150kV NEW PHT 150kV SENAYAN #2 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV NEW PHT 150kV SENAYAN | #2
186 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0018 - PHT 150kV PETUKANGAN #1 | PHT 150kV PETUKANGAN #1 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN | #1 | 150 kV / 100 V |  | MiCom C264 | 33257266/03/15 | Numerik |  | aktif | aktif | tdk aktif | <12 V | >52 V | 6 V | 15
187 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0019 - PHT 150kV PETUKANGAN #2 | PHT 150kV PETUKANGAN #2 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN | #2
214 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-E0001 - KOPEL BUS 150kV | KOPEL BUS 150kV | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | KOPEL BUS |  | 150 kV / 100 V | ABB | REC 650 | T1809134 | Numerik | 2019 | aktif | aktif | tdk aktif | 23.1 | 51.97 | 8.66 | 15 | 0.167
210 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20003 - PHT 150kV ALAM SUTERA #1 | PHT 150kV ALAM SUTERA #1 | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA | #1
211 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20004 - PHT 150kV ALAM SUTERA #2 | PHT 150kV ALAM SUTERA #2 | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA | #2 | 150 kV / 100 V | ABB | REC 650 | T1809125 | Numerik | 2019
212 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20001 - PHT 150kV CURUG #1 | PHT 150kV CURUG #1 | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG | #1
213 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20002 - PHT 150kV CURUG #2 | PHT 150kV CURUG #2 | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG | #2 | 150 kV / 100 V | Alstom | MiCom P545 | 486822x | Numerik | 2019 | aktif | aktif | tdk aktif | 11.5 | 52 | 6 | 15 | 0.167
226 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0082 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL | #1
227 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0075 - PHT 500kV KEMBANGAN #2 | PHT 500kV KEMBANGAN #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN | #2
228 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0076 - PHT 500kV MUARAKARANG #1 | PHT 500kV MUARAKARANG #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG | #1
229 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0077 - PHT 500kV MUARAKARANG #2 | PHT 500kV MUARAKARANG #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG | #2
232 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | FUTURE #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | FUTURE | #1
233 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | FUTURE #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | FUTURE | #2
|  |  |  | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT #1 500/150kV |  | 150 kV / 100 V | Alstom | MAVS | 6338408 |  |  | aktif | aktif | tdk aktif | < 12 | > 52 | 5,7 V | 10 | 0.17
230 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-DUM.000-B0072 - PHT 500kV DURIKOSAMBI #1 | PHT 500kV DURIKOSAMBI #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #1
231 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0018 - PHT 500kV DURIKOSAMBI #2 | PHT 500kV DURIKOSAMBI #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #2
234 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0007 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #1
235 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0008 - PHT 500kV GANDUL #2 | PHT 500kV GANDUL #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #2

## BUSPRO (hidden)
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | ULTG | GI / GITET | MPU | kV | RATIO CT | BUSPRO
[7 empty] | MERK | TYPE | No. SERI | CENTRALIZED/DISTRIBUTED | JENIS RELE | TH OPERASI | STATUS | KETERANGAN | Setting |  |  |  | KET
[15 empty] | I>1 (A) | I>2 (A) | slope k1 | slope k2
| 1 | ULTG ANGKE | GI 150KV ANGKE | MPU | 150 | 4000 / 5 | Alstom | MiCom P746 |  | Centralized | Numerik | 2022 | Aktif | LO Z | 400 | 2400 | 10% | 65%
| 2 | ULTG ANGKE | GI 150KV DADAP | MPU | 150 |  | Alstom | MiCom P743 |  | Distributed | Numerik
| 3 | ULTG ANGKE | GI 150KV MUARAKARANG BARU | MPU | 150 |  | GEC Alsthom | MCAG 34 |  | Centralized | Elektromekanik | 1992 | Aktif | HI Z
| 4 | ULTG ANGKE | GI 150KV MUARAKARANG LAMA | MPU | 150 | 4000 / 5 | Siemens | Reyrolle |  |  | Numerik | 2009 | Aktif | LO Z
| 5 | ULTG ANGKE | GIS 150KV DAAN MOGOT | MPU | 150 |  | ABB | REB 670 |  |  | Numerik | 2018 | Aktif | LO Z
| 6 | ULTG ANGKE | GIS 150KV GROGOL | MPU | 150 |  | GEC Alsthom | MCAG 34 |  |  | Elektromekanik | 2005 | Aktif | HI Z
| 7 | ULTG ANGKE | GIS 150KV GROGOL BARU | MPU | 150 |  | Siemens | 7SS85 |  |  | Numerik | 2020 | Aktif | LO Z
| 8 | ULTG ANGKE | GIS 150KV KEBON JERUK | MPU | 150 |  | GE Alstom | MiCom P746 |  | Centralized | Numerik | 2022 | Aktif | LO Z
| 9 | ULTG ANGKE | GIS 150KV MUARAKARANG BARU | MPU | 150
| 10 | ULTG ANGKE | GIS 150KV NEW SENAYAN | MPU | 150 |  | Areva | MiCom P122 |  |  | Numerik | 2008 | Aktif | HI Z
| 11 | ULTG ANGKE | GIS 150KV PANTAI INDAH KAPUK | MPU | 150 |  | Siemens | 7SS52 |  |  | Numerik | 2016 | Aktif | LO Z
| 12 | ULTG ANGKE | GIS 150KV TOMANG | MPU | 150 |  | Schneider | MiCom P741 |  |  | Numerik | 2021 | Aktif | LO Z
| 13 | ULTG ANGKE | GIS 150KV ULUJAMI | MPU | 150 | 2000 / 1 | GE Alstom | MiCom P746 |  | Centralized | Numerik | 2021 | Aktif |  | 0.03 | 1.2 | 10% | 65%
| 14 | ULTG ANGKE | GISTET 500KV MUARAKARANG BARU | MPU-A | 500
| 15 | ULTG ANGKE | GISTET 500KV MUARAKARANG BARU | MPU-B | 500
| 16 | ULTG CITRA RAYA | GI 150KV CURUG | MPU | 150 | 4000 / 1 | GEC Alsthom | MCAG 34 |  |  | Elektromekanik | 2021 | Aktif | HI Z |  |  |  |  | Buspro Goose
| 17 | ULTG CITRA RAYA | GI 150KV GAJAH TUNGGAL | MPU | 150
| 18 | ULTG CITRA RAYA | GI 150KV ITS | MPU | 150
| 19 | ULTG CITRA RAYA | GI 150KV JATAKE | MPU | 150 | 2000 / 5 | NR | PCS 915 |  |  | Numerik | 2021 | Aktif | LO Z
| 20 | ULTG CITRA RAYA | GI 150KV MAXIMANGANDO | MPU | 150 | [5 empty] | Tidak Ada |  | Tidak Ada
| 21 | ULTG CITRA RAYA | GI 150KV SINDANG JAYA | MPU | 150 | 4000 / 1 | NR | PCS 915 |  |  | Numerik | 2021 | Aktif |  |  | 1.2
| 22 | ULTG CITRA RAYA | GI 150KV TANGERANG BARU | MPU | 150 | 4000 / 1 | Areva | MiCom P741 |  |  | Numerik | 2012 | Tidak Aktif | LO Z
| 23 | ULTG CITRA RAYA | GI 150KV TELUK NAGA | MPU | 150 |  | Areva | MiCom P741 |  |  | Numerik | 2023 | Aktif | LO Z
| 24 | ULTG CITRA RAYA | GIS 150KV JATAKE BARU | MPU | 150 | 4000 / 1 | NR | PCS 915 |  |  | Numerik | 2021 | Aktif | LO Z
| 25 | ULTG CITRA RAYA | GIS 150KV LONTAR | MPU-A | 150 | 3200 / 1 | NR | RCS 915 |  |  | Numerik | 2010 | Aktif | LO Z
| 26 | ULTG CITRA RAYA | GIS 150KV LONTAR | MPU-B | 150 | 3200 / 1 | NR | RCS 915 |  |  | Numerik | 2010 | Aktif | LO Z
| 27 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | MPU | 150 |  | Areva | MiCom P741 |  |  | Numerik | 2012 | Belum Aktif | LO Z
| 28 | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | MPU | 150 |  | Alstom | MiCom P746 |  |  | Numerik | 2018 | Aktif | LO Z
| 29 | ULTG DURIKOSAMBI | GI 150KV CILEDUG | MPU | 150 |  | GEC Alsthom | MCAG 34 |  |  | Elektromekanik | 1995 | Aktif | HI Z
| 30 | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | MPU | 150 |  | GE | B90 | 20349801 |  | Numerik | 2015 | Aktif | LO Z
| 31 | ULTG DURIKOSAMBI | GI 150KV TANGERANG | MPU | 150 |  | Alstom | MiCom P746 |  |  | Numerik | 2022 | Aktif | LO Z
| 32 | ULTG DURIKOSAMBI | GIS 150KV ALAM SUTERA | MPU | 150 | 4000 / 1 | Alstom | MiCom P746 |  |  | Numerik | 2014 | Aktif | LO Z
| 33 | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | MPU | 150 |  | GEC Alsthom | MCAG 34 |  |  | Elektromekanik | 1994 | Aktif | HI Z
| 34 | ULTG DURIKOSAMBI | GIS 150KV SUMMARECON GADING SERPONG | MPU | 150 | 4000 / 1 | ABB | REB 670 | T1809122, T1809123, T1809121 |  | Numerik | 2019 | Aktif | LO Z | 0.03 | 1.2 | 15% | 53%
| 35 | ULTG DURIKOSAMBI | GIS 150KV METLAND | MPU | 150
| 36 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | MPU-A | 500 |  | Alstom | MiCom P746 |  |  | Numerik | 2019 | Aktif | LO Z
| 37 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | MPU-B | 500 |  | GE | B90 |  |  | Numerik | 2019 | Aktif | LO Z
| 38 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | MPU-A | 500 |  | Alstom | MiCom P746 |  |  | Numerik | 2019 | Aktif | LO Z
| 39 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | MPU-B | 500 |  | GE | B90 |  |  | Numerik | 2019 | Aktif | LO Z

## KAPASITOR (hidden)
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
ID | NO | GI / GIS | BAY | BAY | ULTG | GI / GIS | BAY | SIRKIT | kV | MVAR | OCR/GFR | [15 empty] | UNBALANCE | [12 empty] | UVR/OVR | [10 empty] | KET
[11 empty] | RATIO CT | MERK | Type | NO. SERIE | JENIS RELE | TH OPERASI | SETTING | [9 empty] | RATIO CT | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SETTING | [6 empty] | RATIO VT | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SETTING
[17 empty] | In | Is OC | tms | I>> | time | Is GF | tms | I>> | time | karakteristik | [6 empty] | ALARM |  | TRIP |  | I>> | time | karakteristik | [6 empty] | U< | time (s) | U> | time (s) | karakteristik
[33 empty] | Is | time | Is | time
| 1 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0016 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG ANGKE | GI 150KV ANGKE | KAPASITOR SC | #1 | 150kV | 25 | 400 / 5 | Alstom | MiCom P142 |  | Numerik | 2020 | 1 | 1.45 | 300 s | 3.6 | 0.2 | blok | blok | blok | blok | DT |  | Alstom | MiCom P14N |  | Numerik | 2020 |  |  | 0.25 | 0.1 | 0.1 | 5 | DT | 150kV / 100 | Alstom | MiCom P94V |  | Numerik |  | 90 | 100 | 106.7 | 3 | DT
| 2 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0021 - KAPASITOR SC #2 150kV | KAPASITOR SC #2 150kV | ULTG ANGKE | GI 150KV ANGKE | KAPASITOR SC | #2 | 150kV | 25 | 400 / 1 | Alstom | MiCom P142 | 34421654/04/18 | Numerik |  | 1 | 0.29 | 300 s | 0.72 | 0.2 | blok | blok | blok | blok | SI | 200 / 5 | Alstom | MiCom P14N | 344267/04/18 | Numerik |  |  |  | 0.46 | 0.1 | 0.08 | 5 | DT | 150kV / 100 | Alstom | MiCom P94V | 34423266/04/18 | Numerik |  | 90 | 100 | 106.7 | 3 | DT
| 3 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0018 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG CITRA RAYA | GI 150KV JATAKE | KAPASITOR SC | #1 | 150kV | 25 | 400 / 1 | Siemens | 7SJ63 | BF1209066513 | Numerik |  | 5 | 0.29 | 60 | 0.7 | 0.2 | blok | blok | blok | blok | DT |  | Siemens | 7SR120 | 7SR21021AA870C0-CC | Numerik |  |  |  | 0.06 | 5 | 0.46 | 0.1 | DT | 150kV / 100 | Siemens | 7SJ63 | BF1209066513 | Numerik |  | 51.9 | 100 | 63.5 | 3 | DT
| 4 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0019 - KAPASITOR SC #2 150kV | KAPASITOR SC #2 150kV | ULTG CITRA RAYA | GI 150KV JATAKE | KAPASITOR SC | #2 | 150kV | 50 | 300 / 5 | NR | PCR-9611 | NRJB2088871540020 | Numerik |  | 5 | 3.85 | 100 | 9.5 | 0.2 | blok | blok | blok | blok | DT |  | NR | PCR-9611 | NRJB2088871540030 | Numerik |  |  |  | 0.121 | 5 | 0.842 | 0.1 | DT | 150kV / 100 | NR | PCR-9611 | NRJB2088871540040 | Numerik |  | 51.96 | 100 | 61.584 | 3 | DT
| 5 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0012 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG CITRA RAYA | GI 150KV TELUK NAGA | KAPASITOR SC | #1 | 150kV | 25 | 200 / 1 | Alstom | MiCom P123 | 3602765 | Numerik |  | 1 | 0.58 | 0.85 | 6.7 | 0.2 | 0.1 | 1.2 | blok | blok | SI |  | Nokian Capacitors | NUR 36 | I0100235 |  |  |  |  | 0.4 | 0.1 | blok | blok | DT | 150kV / 100 | Alstom | MiCom P922 | 3702380 | Numerik |  | 80 | 5 | 106.6 | 5 | DT
| 6 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0008 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG DURIKOSAMBI | GI 150KV CENGKARENG | KAPASITOR SC | #1 | 150kV | 25 | 200 / 1 | Areva | MiCom | 2505502 | Numerik |  | 1 | 0.58 | 0.9 | 6.7 | 0.2 | 0.1 | 0.1 | blok | blok | SI |  | Nokian Capacitors | NUR 36 |  |  |  | 0.2 | 10 | 0.4 | 0.1
| 7 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-DUM.000-B0086 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG DURIKOSAMBI | GI 150KV CENGKARENG BARU | KAPASITOR SC | #1 | 150kV | [18 empty] | Alstom | MiCom P643 | 33980381/02/17 | Numerik | 2018 |  |  | 0.1 | 0 |  |  | DT
| 8 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0013 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG DURIKOSAMBI | GI 150KV CILEDUG | KAPASITOR SC | #1 | 150kV | 50 | 300 / 1 | NR | PCS-9611 | NRJB2088871542360 | Numerik |  | SETTING In: 1; SETTING Is OC: 0.77; SETTING tms: 100; SETTING I>>: 1.9; SETTING time: 0.2 | SI |  | NR | PCS-9611 | NRJB2088871542350 | Numerik |  |  |  | 0.121 | 5 | 0.842 | 0.1 |  | 150kV / 100 | NR | PCR-9611 | NRJB2088871542370 | Numerik |  | blok | blok | 106.67 | 3 | DT
| 9 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0002 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | KAPASITOR SC | #1 | 150kV | 50 | 400 / 1 | Schneider | MiCom P122 | 36243996/08/13 | Numerik |  | 1 | 0.58 | 150 | 1.4 | 0.2 | 0.08 | 5 | 0.55 | 0.1 | DT |  | Areva | MiCom P120 | 607785 | Numerik |  |  |  | 0.08 | 5 | 0.55 | 0.1 | DT | 150kV / 100 | Areva | MiCom P922 | 2505095 | Numerik
| 10 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0001 - KAPASITOR SC #1 150kV | KAPASITOR SC #1 150kV | ULTG DURIKOSAMBI | GI 150KV TANGERANG | KAPASITOR SC | #1 | 150kV | 25 | 300 / 1 | ABB | REJ 525 | 201073 | Numerik |  | 5 | 0.58 | 0.9 | 7 | 0.21 | 0.1 | 1.26 | blok | blok | SI |  | ABB | SPAJ 160 C |  | Numerik |  |  |  | 0.5 | instant | blok | blok | SI | 150kV / 100 | ABB | REU523 | 201074 | Numerik |  | 105 | 5 | 60 | 5 | DT

## CBF
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
NO | GI / GIS | BAY | BAY | DIAMETER | DIAMETER | ULTG | GI / GIS | BAY | SIRKIT | DIAMETER | PMT | kV | RATIO CT | CBF | [9 empty] | KET
[14 empty] | MERK | Type | NO. SERIE | JENIS RELE | TH OPERASI | SETTING
[19 empty] | In | Iset (mA) | t1 (ms) | t2 (ms) | karakteristik
1 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-008.008-B0008 - 7A1 DIAMETER #1 500kV | 7A1 DIAMETER #1 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7A1 | 500/150kV | 2000 / 1 | Areva | MiCom P821 | 3307182 | Numerik |  | 1 | 200 | 100 | 250
2 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0002 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | TRS-3413-008.008-B0018 - 7A2 DIAMETER #2 500kV | 7A2 DIAMETER #2 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #2 | CUT OFF 1 - DIAMETER #2 | 7A2 | 500/150kV | 2000 / 1 | Areva | MiCom P821 | 3307172 | Numerik |  | 1 | 200 | 100 | 250
3 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0029 - IBT #3 500/150kV (HV) | IBT #3 500/150kV (HV) | TRS-3413-008.008-B0023 - 7A5 DIAMETER #5 500kV | 7A5 DIAMETER #5 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #3 | CUT OFF 1 - DIAMETER #5 | 7A5 | 500/150kV | 1000 / 1 | Siemens | 7VK61 | BF1201064272 | Numerik |  | 1 | 200 | 100 | 250
4 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0030 - IBT #4 500/150kV (HV) | IBT #4 500/150kV (HV) | TRS-3413-008.008-B0026 - 7A6 DIAMETER #6 500kV | 7A6 DIAMETER #6 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #4 | CUT OFF 1 - DIAMETER #6 | 7A6 | 500/150kV | 2000 / 1 | Areva | MiCom P821 | 32687102/10/13 | Numerik |  | 1 | 200 | 100 | 250
5 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0015 - PHT 500kV JAWA 7 #1 | PHT 500kV JAWA 7 #1 | TRS-3413-008.008-B0021 - 7B2 DIAMETER #2 500kV | 7B2 DIAMETER #2 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV JAWA 7 | #1 | CUT OFF 3 - DIAMETER #2 | 7B2 | 500kV | 4000 / 1 | Areva | MiCom P821 | 3307181 | Numerik |  | 1 | 200 | 100 | 250
6 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0014 - PHT 500kV JAWA 7 #2 | PHT 500kV JAWA 7 #2 | TRS-3413-008.008-B0020 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV JAWA 7 | #2 | CUT OFF 3 - DIAMETER #1 | 7B1 | 500kV | 4000 / 1 | Schneider | MiCom P142 | 732190F | Numerik |  | 1 | 200 | 100 | 250
7 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0004 - PHT 500kV LENGKONG #1 | PHT 500kV LENGKONG #1 | TRS-3413-008.008-B0022 - 7A3 DIAMETER #3 500kV | 7A3 DIAMETER #3 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV LENGKONG | #1 | CUT OFF 1 - DIAMETER #3 | 7A3 | 500kV | 4000 / 1 | Areva | MiCom P821 | 3307179 | Numerik |  | 1 | 200 | 100 | 250
8 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0013 - PHT 500kV LENGKONG #2 | PHT 500kV LENGKONG #2 | TRS-3413-008.008-B0001 - 7A4 DIAMETER #4 500kV | 7A4 DIAMETER #4 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV LENGKONG | #2 | CUT OFF 1 - DIAMETER #4 | 7A4 | 500kV | 4000 / 1 | Areva | MiCom P821 | 3307174 | Numerik |  | 1 | 200 | 100 | 250
9 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0005 - PHT 500kV SURALAYA #1 | PHT 500kV SURALAYA #1 | TRS-3413-008.008-B0016 - 7B3 DIAMETER #3 500kV | 7B3 DIAMETER #3 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV SURALAYA | #1 | CUT OFF 3 - DIAMETER #3 | 7B3 | 500kV | 4000 / 1 | Schneider | MiCom P142 | 733531F | Numerik | 2021 | 1 | 100 | 100 | 250
10 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0012 - PHT 500kV SURALAYA #2 | PHT 500kV SURALAYA #2 | TRS-3413-008.008-B0003 - 7B4 DIAMETER #4 500kV | 7B4 DIAMETER #4 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV SURALAYA | #2 | CUT OFF 3 - DIAMETER #4 | 7B4 | 500kV | 4000 / 1 | Areva | MiCom P821 | 3307180 | Numerik |  | 1 | 200 | 100 | 250
11 | TRS-3413-008.008 - GITET 500kV BALARAJA | #N/A | PHT 500kV KEMBANGAN (FUTURE) #1 | TRS-3413-008.008-B0025 - 7B5 DIAMETER #5 500kV | 7B5 DIAMETER #5 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV KEMBANGAN (FUTURE) | #1 | CUT OFF 3 - DIAMETER #5 | 7B5 | 500kV | 2000 / 1 | SIEMENS | 7VK87 | BM1803010496 | Numerik |  | 1 | 200 | 100 | 250
12 | TRS-3413-008.008 - GITET 500kV BALARAJA | #N/A | PHT 500kV KEMBANGAN (FUTURE) #2 | TRS-3413-008.008-B0028 - 7B6 DIAMETER #6 500kV | 7B6 DIAMETER #6 500kV | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV KEMBANGAN (FUTURE) | #2 | CUT OFF 3 - DIAMETER #6 | 7B6 | 500kV | 2000 / 1 | SIEMENS | 7VK87 | BM1803010493 | Numerik |  | 1 | 200 | 100 | 250
13 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0007 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | TRS-3413-008.008-B0007 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #1 | 7AB1 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307173 | Numerik |  | 1 | 200 | 100 | 250
14 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0017 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | TRS-3413-008.008-B0017 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #2 | 7AB2 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307171 | Numerik |  | 1 | 200 | 100 | 250
15 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0019 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | TRS-3413-008.008-B0019 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #3 | 7AB3 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307176 | Numerik |  | 1 | 200 | 100 | 250
16 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0009 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | TRS-3413-008.008-B0009 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #4 | 7AB4 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307177 | Numerik |  | 1 | 200 | 100 | 250
17 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0024 - 7AB5 DIAMETER #5 500kV | 7AB5 DIAMETER #5 500kV | TRS-3413-008.008-B0024 - 7AB5 DIAMETER #5 500kV | 7AB5 DIAMETER #5 500kV | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #5 | 7AB5 | 500kV | 2000 / 1 | Siemens | 7VK61 | BF1201064277 | Numerik |  | 1 | 200 | 100 | 250
18 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0027 - 7AB6 DIAMETER #6 500kV | 7AB6 DIAMETER #6 500kV | TRS-3413-008.008-B0027 - 7AB6 DIAMETER #6 500kV | 7AB6 DIAMETER #6 500kV | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #6 | 7AB6 | 500kV | 2000 / 1 | Areva | MiCom P821 | 32687103/10/13 | Numerik |  | 1 | 200 | 100 | 250
19 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0001 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-194.194-B0009 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT | #1 | CUT OFF 3 - DIAMETER #1 | 7B1 | 500/150kV
20 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0004 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | TRS-3413-194.194-B0010 - 7B2 DIAMETER #2 500kV | 7B2 DIAMETER #2 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT | #2 | CUT OFF 3 - DIAMETER #2 | 7B2 | 500/150kV
21 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0082 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | TRS-3413-194.194-B0008 - 7A4 DIAMETER #4 500kV | 7A4 DIAMETER #4 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL | #1 | CUT OFF 1 - DIAMETER #4 | 7A4 | 500kV
22 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0075 - PHT 500kV KEMBANGAN #2 | PHT 500kV KEMBANGAN #2 | TRS-3413-194.194-B0007 - 7A3 DIAMETER #3 500kV | 7A3 DIAMETER #3 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN | #2 | CUT OFF 1 - DIAMETER #3 | 7A3 | 500kV
23 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | IBT (FUTURE) #3 500/150kV (HV) | TRS-3413-194.194-B0011 - 7B3 DIAMETER #3 500kV | 7B3 DIAMETER #3 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT (FUTURE) | #3 | CUT OFF 3 - DIAMETER #3 | 7B3 | 500/150kV
24 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | IBT (FUTURE) #4 500/150kV (HV) | TRS-3413-194.194-B0012 - 7B4 DIAMETER #4 500kV | 7B4 DIAMETER #4 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT (FUTURE) | #4 | CUT OFF 3 - DIAMETER #4 | 7B4 | 500/150kV
25 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | PHT 500kV MUARAKARANG (FUTURE) #1 | TRS-3413-194.194-B0006 - 7A2 DIAMETER #2 500kV | 7A2 DIAMETER #2 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG (FUTURE) | #1 | CUT OFF 1 - DIAMETER #2 | 7A2 | 500kV
26 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | PHT 500kV MUARAKARANG (FUTURE) #2 | TRS-3413-194.194-B0005 - 7A1 DIAMETER #1 500kV | 7A1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG (FUTURE) | #2 | CUT OFF 1 - DIAMETER #1 | 7A1 | 500kV
27 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | 7AB1 7AB1 DIAMETER #1 500kV 500kVkV | TRS-3413-194.194-B0013 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #1 | 7AB1 | 500kV
28 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | 7AB2 7AB2 DIAMETER #2 500kV 500kVkV | TRS-3413-194.194-B0014 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #2 | 7AB2 | 500kV
29 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | 7AB3 7AB3 DIAMETER #3 500kV 500kVkV | TRS-3413-194.194-B0015 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #3 | 7AB3 | 500kV
30 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | 7AB4 7AB4 DIAMETER #4 500kV 500kVkV | TRS-3413-194.194-B0016 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #4 | 7AB4 | 500kV
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-004.004-B0001 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7AB1 | 500/150kV | 1000 / 1 | GEC Alstom | MCGG | 633932B | Elektromekanik |  | 1 | 0.1 | instant | instant | Definite | CBF 1
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-004.004-B0001 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7AB1 | 500/150kV | 1000 / 1 | GEC Alstom | MCGG | 633933B | Elektromekanik |  | 1 | 0.1 | instant | instant | Definite | CBF 2
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-004.004-B0002 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7B1 | 500/150kV | 1000 / 1 | GEC Alstom | MCGG | 633922B | Elektromekanik |  | 1 | 0.1 | instant | instant | Definite | CBF 1
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-004.004-B0002 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7B1 | 500/150kV | 1000 / 1 | GEC Alstom | MCGG | 633923B | Elektromekanik |  | 1 | 0.1 | instant | instant | Definite | CBF 2
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | #N/A | 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 |  |  | 500/150kV | 2000 / 5 | GEC Alstom | MCGG | 633903B | Elektromekanik |  | 1 | 0.1 | instant | instant | Definite | CBF 1
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | #N/A | 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 |  |  | 500/150kV | 2000 / 5 | GEC Alstom | MCGG | 633904B | Elektromekanik |  | 1 | 0.1 | instant | instant | Definite | CBF 2
32 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0005 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | TRS-3413-004.004-B0003 - 7A2 DIAMETER #2 500kV | 7A2 DIAMETER #2 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #2 | CUT OFF 1 - DIAMETER #2 | 7A2 | 500/150kV |  | GEC | MCTI 39 |  | Elektromekanik |  |  | 0.5
33 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-DUM.000-B0072 - PHT 500kV DURIKOSAMBI #1 | PHT 500kV DURIKOSAMBI #1 | TRS-3413-DUM.000-B0054 - 7B3 DIAMETER #3 500kV | 7B3 DIAMETER #3 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #1 | CUT OFF 3 - DIAMETER #3 | 7B3 | 500kV
34 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0018 - PHT 500kV DURIKOSAMBI #2 | PHT 500kV DURIKOSAMBI #2 | TRS-3413-004.004-B0017 - 7B4 DIAMETER #4 500kV | 7B4 DIAMETER #4 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #2 | CUT OFF 3 - DIAMETER #4 | 7B4 | 500kV
35 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0007 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | TRS-3413-004.004-B0002 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #1 | CUT OFF 3 - DIAMETER #1 | 7B1 | 500kV
36 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0008 - PHT 500kV GANDUL #2 | PHT 500kV GANDUL #2 | TRS-3413-004.004-B0011 - 7B2 DIAMETER #2 500kV | 7B2 DIAMETER #2 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #2 | CUT OFF 3 - DIAMETER #2 | 7B2 | 500kV
37 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | PHT 500kV BALARAJA (FUTURE) #1 | TRS-3413-004.004-B0015 - 7A4 DIAMETER #4 500kV | 7A4 DIAMETER #4 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA (FUTURE) | #1 | CUT OFF 1 - DIAMETER #4 | 7A4 | 500kV
38 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | PHT 500kV BALARAJA (FUTURE) #2 | TRS-3413-004.004-B0013 - 7A3 DIAMETER #3 500kV | 7A3 DIAMETER #3 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA (FUTURE) | #2 | CUT OFF 1 - DIAMETER #3 | 7A3 | 500kV
39 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | 7AB1 7AB1 DIAMETER #1 500kV 500kVkV | TRS-3413-004.004-B0001 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #1 | 7AB1 | 500kV
40 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | 7AB2 7AB2 DIAMETER #2 500kV 500kVkV | TRS-3413-004.004-B0004 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #2 | 7AB2 | 500kV
41 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | 7AB3 7AB3 DIAMETER #3 500kV 500kVkV | TRS-3413-004.004-B0014 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #3 | 7AB3 | 500kV
42 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | 7AB4 7AB4 DIAMETER #4 500kV 500kVkV | TRS-3413-004.004-B0016 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #4 | 7AB4 | 500kV
43 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0007 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | TRF | #1 |  |  | 150/20kV
44 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0008 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | TRF | #2 |  |  | 150/20kV
45 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0009 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | TRF | #3 |  |  | 150/20kV
46 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0010 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | TRF | #4 |  |  | 150/20kV
47 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0005 - PHT 150kV ANCOL #1 | PHT 150kV ANCOL #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV ANCOL | #1 |  |  | 150kV
48 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0002 - PHT 150kV ANCOL #2 | PHT 150kV ANCOL #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV ANCOL | #2 |  |  | 150kV
49 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0012 - PHT 150kV KARET LAMA #1 | PHT 150kV KARET LAMA #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KARET LAMA | #1 |  |  | 150kV
50 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0013 - PHT 150kV KARET LAMA #2 | PHT 150kV KARET LAMA #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KARET LAMA | #2 |  |  | 150kV
51 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0001 - PHT 150kV KETAPANG #1 | PHT 150kV KETAPANG #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KETAPANG | #1 |  |  | 150kV
52 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0004 - PHT 150kV KETAPANG #2 | PHT 150kV KETAPANG #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV KETAPANG | #2 |  |  | 150kV
53 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0014 - PHT 150kV MUARAKARANG LAMA #1 | PHT 150kV MUARAKARANG LAMA #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA | #1 |  |  | 150kV
54 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-074.074-B0015 - PHT 150kV MUARAKARANG LAMA #2 | PHT 150kV MUARAKARANG LAMA #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV MUARAKARANG LAMA | #2 |  |  | 150kV
55 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-DUM.000-B0008 - PHT 150kV UGC MUARAKARANG LAMA #1 | PHT 150kV UGC MUARAKARANG LAMA #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA | #1 |  |  | 150kV
56 | TRS-3413-074.074 - GI 150kV ANGKE | TRS-3413-DUM.000-B0009 - PHT 150kV UGC MUARAKARANG LAMA #2 | PHT 150kV UGC MUARAKARANG LAMA #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV ANGKE | PHT 150kV UGC MUARAKARANG LAMA | #2 |  |  | 150kV
57 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0009 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | TRF | #1 |  |  | 150/20kV
58 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0010 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | TRF | #2 |  |  | 150/20kV
59 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0016 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | TRF | #3 |  |  | 150/20kV
60 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0014 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | TRF | #4 |  |  | 150/20kV
61 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0006 - PHT 150kV CIKANDE #1 | PHT 150kV CIKANDE #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | PHT 150kV CIKANDE | #1 |  |  | 150kV
62 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0005 - PHT 150kV CIKANDE #2 | PHT 150kV CIKANDE #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | PHT 150kV CIKANDE | #2 |  |  | 150kV
63 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0007 - PHT 150kV SUVARNA SUTERA #1 | PHT 150kV SUVARNA SUTERA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | PHT 150kV SUVARNA SUTERA | #1 |  |  | 150kV
64 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0008 - PHT 150kV SUVARNA SUTERA #2 | PHT 150kV SUVARNA SUTERA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | PHT 150kV SUVARNA SUTERA | #2 |  |  | 150kV
65 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0001 - PHT 150kV NEW BALARAJA #1 | PHT 150kV NEW BALARAJA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | PHT 150kV NEW BALARAJA | #1 |  |  | 150kV
66 | TRS-3413-047.047 - GI 150kV BALARAJA | TRS-3413-047.047-B0002 - PHT 150kV NEW BALARAJA #2 | PHT 150kV NEW BALARAJA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV BALARAJA | PHT 150kV NEW BALARAJA | #2 |  |  | 150kV
67 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0019 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | TRF | #1 |  |  | 150/20kV
68 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0020 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | TRF | #2 |  |  | 150/20kV
69 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0003 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | TRF | #3 |  |  | 150/20kV
70 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0004 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | TRF | #4 |  |  | 150/20kV
71 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0001 - TRF #5 150/20kV | TRF #5 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | TRF | #5 |  |  | 150/20kV
72 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0013 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI | #1 |  |  | 150kV
73 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0014 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | PHT 150kV DURIKOSAMBI | #2 |  |  | 150kV
74 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0016 - PHT 150kV TANGERANG #1 | PHT 150kV TANGERANG #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | PHT 150kV TANGERANG | #1 |  |  | 150kV
75 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0015 - PHT 150kV TANGERANG #2 | PHT 150kV TANGERANG #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | PHT 150kV TANGERANG | #2 |  |  | 150kV
76 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0017 - PHT 150kV CENGKARENG BARU #1 | PHT 150kV CENGKARENG BARU #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU | #1 |  |  | 150kV
77 | TRS-3413-060.060 - GI 150kV CENGKARENG | TRS-3413-060.060-B0018 - PHT 150kV CENGKARENG BARU #2 | PHT 150kV CENGKARENG BARU #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG | PHT 150kV CENGKARENG BARU | #2 |  |  | 150kV
78 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG BARU | TRF | #1 |  |  | 150/20kV
79 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG BARU | TRF | #2 |  |  | 150/20kV
80 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0006 - PHT 150kV CENGKARENG #1 | PHT 150kV CENGKARENG #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG | #1 |  |  | 150kV
81 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0007 - PHT 150kV CENGKARENG #2 | PHT 150kV CENGKARENG #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG BARU | PHT 150kV CENGKARENG | #2 |  |  | 150kV
82 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0004 - PHT 150kV TANGERANG BARU #1 | PHT 150kV TANGERANG BARU #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #1 |  |  | 150kV
83 | TRS-3413-065.065 - GI 150kV CENGKARENG BARU | TRS-3413-065.065-B0005 - PHT 150kV TANGERANG BARU #2 | PHT 150kV TANGERANG BARU #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CENGKARENG BARU | PHT 150kV TANGERANG BARU | #2 |  |  | 150kV
84 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | TRF | #1 |  |  | 150/20kV
85 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | TRF | #2 |  |  | 150/20kV
86 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0017 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | TRF | #3 |  |  | 150/20kV
87 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0005 - PHT 150kV CURUG #1 | PHT 150kV CURUG #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV CURUG | #1 |  |  | 150kV
88 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0006 - PHT 150kV CURUG #2 | PHT 150kV CURUG #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV CURUG | #2 |  |  | 150kV
89 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0003 - PHT 150kV SUVARNA SUTERA #1 | PHT 150kV SUVARNA SUTERA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV SUVARNA SUTERA | #1 |  |  | 150kV
90 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0004 - PHT 150kV SUVARNA SUTERA #2 | PHT 150kV SUVARNA SUTERA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV SUVARNA SUTERA | #2 |  |  | 150kV
91 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0007 - PHT 150kV JATAKE #1 | PHT 150kV JATAKE #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV JATAKE | #1 |  |  | 150kV
92 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0014 - PHT 150kV JATAKE #2 | PHT 150kV JATAKE #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV JATAKE | #2 |  |  | 150kV
93 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0013 - PHT 150kV PASAR KEMIS #1 | PHT 150kV PASAR KEMIS #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV PASAR KEMIS | #1 |  |  | 150kV
94 | TRS-3413-048.048 - GI 150kV CIKUPA | TRS-3413-048.048-B0012 - PHT 150kV PASAR KEMIS #2 | PHT 150kV PASAR KEMIS #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CIKUPA | PHT 150kV PASAR KEMIS | #2 |  |  | 150kV
95 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0009 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | TRF | #1 |  |  | 150/20kV
96 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | TRF | #2 |  |  | 150/20kV
97 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0011 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | TRF | #3 |  |  | 150/20kV
98 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0014 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | TRF | #4 |  |  | 150/20kV
99 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0001 - PHT 150kV ALAM SUTERA #1 | PHT 150kV ALAM SUTERA #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA | #1 |  |  | 150kV
100 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0017 - PHT 150kV ALAM SUTERA #2 | PHT 150kV ALAM SUTERA #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | PHT 150kV ALAM SUTERA | #2 |  |  | 150kV
101 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0004 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | PHT 150kV KEMBANGAN | #1 |  |  | 150kV
102 | TRS-3413-054.054 - GI 150kV CILEDUG | TRS-3413-054.054-B0016 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CILEDUG | PHT 150kV KEMBANGAN | #2 |  |  | 150kV
103 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0014 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | TRF | #1 |  |  | 150/20kV
104 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0001 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | TRF | #2 |  |  | 150/20kV
105 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0010 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | TRF | #3 |  |  | 150/20kV
106 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0018 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | TRF | #4 |  |  | 150/20kV
107 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0005 - PHT 150kV LEGOK #1 | PHT 150kV LEGOK #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | PHT 150kV LEGOK | #1 |  |  | 150kV
108 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0006 - PHT 150kV LEGOK #2 | PHT 150kV LEGOK #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | PHT 150kV LEGOK | #2 |  |  | 150kV
109 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0016 - PHT 150kV MILENIUM #1 | PHT 150kV MILENIUM #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | PHT 150kV MILENIUM | #1 |  |  | 150kV
110 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0002 - PHT 150kV MILENIUM #2 | PHT 150kV MILENIUM #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | PHT 150kV MILENIUM | #2 |  |  | 150kV
111 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0003 - PHT 150kV TIGARAKSA #1 | PHT 150kV TIGARAKSA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | PHT 150kV TIGARAKSA | #1 |  |  | 150kV
112 | TRS-3413-051.051 - GI 150kV CITRA HABITAT | TRS-3413-051.051-B0004 - PHT 150kV TIGARAKSA #2 | PHT 150kV TIGARAKSA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV CITRA HABITAT | PHT 150kV TIGARAKSA | #2 |  |  | 150kV
113 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0009 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | TRF | #1 |  |  | 150/20kV
114 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0001 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | TRF | #2 |  |  | 150/20kV
115 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0010 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | TRF | #3 |  |  | 150/20kV
116 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0012 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | TRF | #4 |  |  | 150/20kV
117 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0008 - PHT 150kV CIKUPA #1 | PHT 150kV CIKUPA #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | PHT 150kV CIKUPA | #1 |  |  | 150kV
118 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-DUM.000-B0012 - PHT 150kV CIKUPA #2 | PHT 150kV CIKUPA #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | PHT 150kV CIKUPA | #2 |  |  | 150kV
119 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-143.143-B0003 - PHT 150kV SUMMARECON GADING SERPONG #1 | PHT 150kV SUMMARECON GADING SERPONG #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG | #1 |  |  | 150kV
120 | TRS-3413-143.143 - GI 150kV CURUG | TRS-3413-DUM.000-B0013 - PHT 150kV SUMMARECON GADING SERPONG #2 | PHT 150kV SUMMARECON GADING SERPONG #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV CURUG | PHT 150kV SUMMARECON GADING SERPONG | #2 |  |  | 150kV
121 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0010 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | TRF | #1 |  |  | 150/20kV
122 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0011 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | TRF | #2 |  |  | 150/20kV
123 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0012 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | TRF | #3 |  |  | 150/20kV
124 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0007 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | TRF | #4 |  |  | 150/20kV
125 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0031 - TRF #5 150/20kV | TRF #5 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | TRF | #5 |  |  | 150/20kV
126 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0023 - PHT 150kV CENGKARENG #1 | PHT 150kV CENGKARENG #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG | #1 |  |  | 150kV
127 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0022 - PHT 150kV CENGKARENG #2 | PHT 150kV CENGKARENG #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV CENGKARENG | #2 |  |  | 150kV
128 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0008 - PHT 150kV GROGOL BARU #1 | PHT 150kV GROGOL BARU #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU | #1 |  |  | 150kV
129 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0009 - PHT 150kV GROGOL BARU #2 | PHT 150kV GROGOL BARU #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV GROGOL BARU | #2 |  |  | 150kV
130 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0021 - PHT 150kV KEBON JERUK #1 | PHT 150kV KEBON JERUK #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK | #1 |  |  | 150kV
131 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0004 - PHT 150kV KEBON JERUK #2 | PHT 150kV KEBON JERUK #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEBON JERUK | #2 |  |  | 150kV
132 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0026 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN | #1 |  |  | 150kV
133 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0027 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV KEMBANGAN | #2 |  |  | 150kV
134 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0006 - PHT 150kV LMK | PHT 150kV LMK | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV LMK |  |  |  | 150kV
135 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0018 - PHT 150kV MUARAKARANG LAMA #1 | PHT 150kV MUARAKARANG LAMA #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV MUARAKARANG LAMA | #1 |  |  | 150kV
136 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0003 - PHT 150kV MUARAKARANG LAMA #2 | PHT 150kV MUARAKARANG LAMA #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV MUARAKARANG LAMA | #2 |  |  | 150kV
137 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0038 - PHT 150kV DAAN MOGOT #1 | PHT 150kV DAAN MOGOT #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT | #1 |  |  | 150kV
138 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0039 - PHT 150kV DAAN MOGOT #2 | PHT 150kV DAAN MOGOT #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV DAAN MOGOT | #2 |  |  | 150kV
139 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0030 - PHT 150kV PETUKANGAN #1 | PHT 150kV PETUKANGAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV PETUKANGAN | #1 |  |  | 150kV
140 | TRS-3413-062.062 - GI 150kV DURIKOSAMBI | TRS-3413-062.062-B0017 - PHT 150kV PETUKANGAN #2 | PHT 150kV PETUKANGAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GI 150KV DURIKOSAMBI | PHT 150kV PETUKANGAN | #2 |  |  | 150kV
141 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0015 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | TRF | #1 |  |  | 150/20kV
142 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | TRF | #2 |  |  | 150/20kV
143 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0001 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | TRF | #3 |  |  | 150/20kV
144 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0016 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | TRF | #4 |  |  | 150/20kV
145 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0020 - TRF #5 150/20kV | TRF #5 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | TRF | #5 |  |  | 150/20kV
146 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0013 - PHT 150kV MAXIMANGANDO #1 | PHT 150kV MAXIMANGANDO #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO | #1 |  |  | 150kV
147 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0014 - PHT 150kV MAXIMANGANDO #2 | PHT 150kV MAXIMANGANDO #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | PHT 150kV MAXIMANGANDO | #2 |  |  | 150kV
148 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0012 - PHT 150kV TANGERANG #1 | PHT 150kV TANGERANG #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | PHT 150kV TANGERANG | #1 |  |  | 150kV
149 | TRS-3413-055.055 - GI 150kV JATAKE | TRS-3413-055.055-B0011 - PHT 150kV TANGERANG #2 | PHT 150kV TANGERANG #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV JATAKE | PHT 150kV TANGERANG | #2 |  |  | 150kV
150 | - GIS 150kV JATAKE BARU | #N/A | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV JATAKE BARU | TRF | #1 |  |  | 150/20kV | 300 / 1 | NR | PCS-921 |  | Numerik | 2021 | 1 | 200 | 150 | 250
151 | - GIS 150kV JATAKE BARU | #N/A | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV JATAKE BARU | TRF | #2 |  |  | 150/20kV | 300 / 1 | NR | PCS-921 |  | Numerik | 2021 | 1 | 200 | 150 | 250
152 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV JATAKE #1 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV JATAKE BARU | PHT 150kV JATAKE | #1 |  |  | 150kV | 2000 / 1 | NR | PCS-921 |  | Numerik | 2021 | 1 | 200 | 150 | 250
153 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV JATAKE #2 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV JATAKE BARU | PHT 150kV JATAKE | #2 |  |  | 150kV | 2000 / 1 | NR | PCS-921 |  | Numerik | 2021 | 1 | 200 | 150 | 250
154 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV TANGERANG #1 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG | #1 |  |  | 150kV | 2000 / 1 | NR | PCS-921 |  | Numerik | 2021 | 1 | 200 | 150 | 250
155 | - GIS 150kV JATAKE BARU | #N/A | PHT 150kV TANGERANG #2 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV JATAKE BARU | PHT 150kV TANGERANG | #2 |  |  | 150kV | 2000 / 1 | NR | PCS-921 |  | Numerik | 2021 | 1 | 200 | 150 | 250
156 | TRS-3413-534.534 - GI 150kV LAUTAN STEEL | TRS-3413-534.534-B0001 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV LAUTAN STEEL | TRF | #1 |  |  | 150/20kV
157 | TRS-3413-534.534 - GI 150kV LAUTAN STEEL | TRS-3413-534.534-B0002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV LAUTAN STEEL | TRF | #2 |  |  | 150/20kV
158 | TRS-3413-534.534 - GI 150kV LAUTAN STEEL | TRS-3413-534.534-B0007 - PHT 150kV SPINMILL #1 | PHT 150kV SPINMILL #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV LAUTAN STEEL | PHT 150kV SPINMILL | #1 |  |  | 150kV
159 | TRS-3413-534.534 - GI 150kV LAUTAN STEEL | TRS-3413-534.534-B0008 - PHT 150kV SPINMILL #2 | PHT 150kV SPINMILL #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV LAUTAN STEEL | PHT 150kV SPINMILL | #2 |  |  | 150kV
160 | TRS-3413-534.534 - GI 150kV LAUTAN STEEL | TRS-3413-534.534-B0005 - PHT 150kV NEW BALARAJA #1 | PHT 150kV NEW BALARAJA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV LAUTAN STEEL | PHT 150kV NEW BALARAJA | #1 |  |  | 150kV
161 | TRS-3413-534.534 - GI 150kV LAUTAN STEEL | TRS-3413-534.534-B0006 - PHT 150kV NEW BALARAJA #2 | PHT 150kV NEW BALARAJA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV LAUTAN STEEL | PHT 150kV NEW BALARAJA | #2 |  |  | 150kV
162 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV MAXIMANGANDO | TRF | #1 |  |  | 150/20kV
163 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV MAXIMANGANDO | TRF | #2 |  |  | 150/20kV
164 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0006 - PHT 150kV JATAKE #1 | PHT 150kV JATAKE #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE | #1 |  |  | 150kV
165 | TRS-3413-056.056 - GI 150kV MAXIMANGANDO | TRS-3413-056.056-B0007 - PHT 150kV JATAKE #2 | PHT 150kV JATAKE #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV MAXIMANGANDO | PHT 150kV JATAKE | #2 |  |  | 150kV
166 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0007 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | TRF | #1 |  |  | 150/20kV
167 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0054 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | TRF | #2 |  |  | 150/20kV
168 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0058 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | TRF | #3 |  |  | 150/20kV
169 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0012 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | TRF | #4 |  |  | 150/20kV
170 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0005 - PHT 150kV CITRA HABITAT #1 | PHT 150kV CITRA HABITAT #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | PHT 150kV CITRA HABITAT | #1 |  |  | 150kV
171 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0006 - PHT 150kV CITRA HABITAT #2 | PHT 150kV CITRA HABITAT #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | PHT 150kV CITRA HABITAT | #2 |  |  | 150kV
172 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0001 - PHT 150kV SPINMILL #1 | PHT 150kV SPINMILL #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | PHT 150kV SPINMILL | #1 |  |  | 150kV
173 | TRS-3413-549.549 - GI 150kV MILENIUM | TRS-3413-549.549-B0002 - PHT 150kV SPINMILL #2 | PHT 150kV SPINMILL #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV MILENIUM | PHT 150kV SPINMILL | #2 |  |  | 150kV
174 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0022 - PHT 150kV PANTAI INDAH KAPUK #1 | PHT 150kV PANTAI INDAH KAPUK #1 | TRS-3413-072.072-B0029 - 5B4 DIAMETER #4 150kV | 5B4 DIAMETER #4 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK | #1 | CUT OFF 3 - DIAMETER #4 | 5B4 | 150kV
175 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0013 - PHT 150kV PANTAI INDAH KAPUK #2 | PHT 150kV PANTAI INDAH KAPUK #2 | TRS-3413-072.072-B0026 - 5B3 DIAMETER #3 150kV | 5B3 DIAMETER #3 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU | PHT 150kV PANTAI INDAH KAPUK | #2 | CUT OFF 3 - DIAMETER #3 | 5B3 | 150kV
176 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0002 - TRF #1 150/20kV | TRF #1 150/20kV | TRS-3413-072.072-B0037 - 5B6 DIAMETER #6 150kV | 5B6 DIAMETER #6 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU | TRF | #1 | CUT OFF 3 - DIAMETER #6 | 5B6 | 150/20kV
177 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0015 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 5B7 DIAMETER #7 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU | TRF | #2 | CUT OFF 3 - DIAMETER #7 | 5B7 | 150/20kV
178 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | TRS-3413-072.072-B0021 - TRF #3 150/20kV | TRF #3 150/20kV | TRS-3413-072.072-B0023 - 5A7 DIAMETER #7 150kV | 5A7 DIAMETER #7 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU | TRF | #3 | CUT OFF 1 - DIAMETER #7 | 5A7 | 150/20kV
179 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5B5 5B5 DIAMETER #5 150kV 150kVkV | TRS-3413-072.072-B0030 - 5B5 DIAMETER #5 150kV | 5B5 DIAMETER #5 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 3 - DIAMETER #5 | 5B5 | 150kV
180 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5A6 5A6 DIAMETER #6 150kV 150kVkV | TRS-3413-072.072-B0036 - 5A6 DIAMETER #6 150kV | 5A6 DIAMETER #6 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 1 - DIAMETER #6 | 5A6 | 150kV
181 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5A5 5A5 DIAMETER #5 150kV 150kVkV | TRS-3413-072.072-B0035 - 5A5 DIAMETER #5 150kV | 5A5 DIAMETER #5 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 1 - DIAMETER #5 | 5A5 | 150kV
182 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5A4 5A4 DIAMETER #4 150kV 150kVkV | TRS-3413-072.072-B0028 - 5A4 DIAMETER #4 150kV | 5A4 DIAMETER #4 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 1 - DIAMETER #4 | 5A4 | 150kV
183 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5A3 5A3 DIAMETER #3 150kV 150kVkV | TRS-3413-072.072-B0027 - 5A3 DIAMETER #3 150kV | 5A3 DIAMETER #3 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 1 - DIAMETER #3 | 5A3 | 150kV
184 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5AB3 5AB3 DIAMETER #3 150kV 150kVkV | TRS-3413-072.072-B0019 - 5AB3 DIAMETER #3 150kV | 5AB3 DIAMETER #3 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 2 - DIAMETER #3 | 5AB3 | 150kV
185 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5AB4 5AB4 DIAMETER #4 150kV 150kVkV | TRS-3413-072.072-B0020 - 5AB4 DIAMETER #4 150kV | 5AB4 DIAMETER #4 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 2 - DIAMETER #4 | 5AB4 | 150kV
186 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5AB5 5AB5 DIAMETER #5 150kV 150kVkV | TRS-3413-072.072-B0003 - 5AB5 DIAMETER #5 150kV | 5AB5 DIAMETER #5 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 2 - DIAMETER #5 | 5AB5 | 150kV
187 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5AB6 5AB6 DIAMETER #6 150kV 150kVkV | TRS-3413-072.072-B0004 - 5AB6 DIAMETER #6 150kV | 5AB6 DIAMETER #6 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 2 - DIAMETER #6 | 5AB6 | 150kV
188 | TRS-3413-072.072 - GI 150kV MUARAKARANG BARU | #N/A | 5AB7 5AB7 DIAMETER #7 150kV 150kVkV | TRS-3413-072.072-B0016 - 5AB7 DIAMETER #7 150kV | 5AB7 DIAMETER #7 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG BARU |  |  | CUT OFF 2 - DIAMETER #7 | 5AB7 | 150kV
189 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0045 - PHT 150kV ANGKE #1 | PHT 150kV ANGKE #1 | TRS-3413-073.073-B0009 - 5B1 DIAMETER #1 150kV | 5B1 DIAMETER #1 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE | #1 | CUT OFF 3 - DIAMETER #1 | 5B1 | 150kV
190 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0046 - PHT 150kV ANGKE #2 | PHT 150kV ANGKE #2 | TRS-3413-073.073-B0010 - 5B2 DIAMETER #2 150kV | 5B2 DIAMETER #2 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV ANGKE | #2 | CUT OFF 3 - DIAMETER #2 | 5B2 | 150kV
191 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0034 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | TRS-3413-073.073-B0011 - 5B3 DIAMETER #3 150kV | 5B3 DIAMETER #3 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV DURIKOSAMBI | #1 | CUT OFF 3 - DIAMETER #3 | 5B3 | 150kV
192 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0039 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | TRS-3413-073.073-B0012 - 5B4 DIAMETER #4 150kV | 5B4 DIAMETER #4 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV DURIKOSAMBI | #2 | CUT OFF 3 - DIAMETER #4 | 5B4 | 150kV
193 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0035 - PHT 150kV BUDIKEMULYAN #1 | PHT 150kV BUDIKEMULYAN #1 | TRS-3413-073.073-B0013 - 5B5 DIAMETER #5 150kV | 5B5 DIAMETER #5 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN | #1 | CUT OFF 3 - DIAMETER #5 | 5B5 | 150kV
194 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0040 - PHT 150kV BUDIKEMULYAN #2 | PHT 150kV BUDIKEMULYAN #2 | TRS-3413-073.073-B0014 - 5B6 DIAMETER #6 150kV | 5B6 DIAMETER #6 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV BUDIKEMULYAN | #2 | CUT OFF 3 - DIAMETER #6 | 5B6 | 150kV
195 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0041 - PHT 150kV MUARAKARANG BARU #1 | PHT 150kV MUARAKARANG BARU #1 | TRS-3413-073.073-B0008 - 5A8 DIAMETER #8 150kV | 5A8 DIAMETER #8 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU | #1 | CUT OFF 1 - DIAMETER #8 | 5A8 | 150kV
196 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0042 - PHT 150kV MUARAKARANG BARU #2 | PHT 150kV MUARAKARANG BARU #2 | TRS-3413-073.073-B0016 - 5B8 DIAMETER #8 150kV | 5B8 DIAMETER #8 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV MUARAKARANG BARU | #2 | CUT OFF 3 - DIAMETER #8 | 5B8 | 150kV
197 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-DUM.000-B0084 - PHT 150kV UGC ANGKE #1 | PHT 150kV UGC ANGKE #1 | TRS-3413-073.073-B0050 - 5A12 DIAMETER #12 150kV | 5A12 DIAMETER #12 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE | #1 | CUT OFF 1 - DIAMETER #12 | 5A12 | 150kV
198 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-DUM.000-B0085 - PHT 150kV UGC ANGKE #2 | PHT 150kV UGC ANGKE #2 | TRS-3413-073.073-B0047 - 5A11 DIAMETER #11 150kV | 5A11 DIAMETER #11 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA | PHT 150kV UGC ANGKE | #2 | CUT OFF 1 - DIAMETER #11 | 5A11 | 150kV
199 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0015 - 5B7 DIAMETER #7 150kV | 5B7 DIAMETER #7 150kV | TRS-3413-073.073-B0015 - 5B7 DIAMETER #7 150kV | 5B7 DIAMETER #7 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 3 - DIAMETER #7 | 5B7 | 150kV
200 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0001 - 5A1 DIAMETER #1 150kV | 5A1 DIAMETER #1 150kV | TRS-3413-073.073-B0001 - 5A1 DIAMETER #1 150kV | 5A1 DIAMETER #1 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #1 | 5A1 | 150kV
201 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0002 - 5A2 DIAMETER #2 150kV | 5A2 DIAMETER #2 150kV | TRS-3413-073.073-B0002 - 5A2 DIAMETER #2 150kV | 5A2 DIAMETER #2 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #2 | 5A2 | 150kV
202 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0003 - 5A3 DIAMETER #3 150kV | 5A3 DIAMETER #3 150kV | TRS-3413-073.073-B0003 - 5A3 DIAMETER #3 150kV | 5A3 DIAMETER #3 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #3 | 5A3 | 150kV
203 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0004 - 5A4 DIAMETER #4 150kV | 5A4 DIAMETER #4 150kV | TRS-3413-073.073-B0004 - 5A4 DIAMETER #4 150kV | 5A4 DIAMETER #4 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #4 | 5A4 | 150kV
204 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0005 - 5A5 DIAMETER #5 150kV | 5A5 DIAMETER #5 150kV | TRS-3413-073.073-B0005 - 5A5 DIAMETER #5 150kV | 5A5 DIAMETER #5 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #5 | 5A5 | 150kV
205 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0006 - 5A6 DIAMETER #6 150kV | 5A6 DIAMETER #6 150kV | TRS-3413-073.073-B0006 - 5A6 DIAMETER #6 150kV | 5A6 DIAMETER #6 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #6 | 5A6 | 150kV
206 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0007 - 5A7 DIAMETER #7 150kV | 5A7 DIAMETER #7 150kV | TRS-3413-073.073-B0007 - 5A7 DIAMETER #7 150kV | 5A7 DIAMETER #7 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #7 | 5A7 | 150kV
207 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0029 - 5A9 DIAMETER #9 150kV | 5A9 DIAMETER #9 150kV | TRS-3413-073.073-B0029 - 5A9 DIAMETER #9 150kV | 5A9 DIAMETER #9 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #9 | 5A9 | 150kV
208 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0030 - 5A10 DIAMETER #10 150kV | 5A10 DIAMETER #10 150kV | TRS-3413-073.073-B0030 - 5A10 DIAMETER #10 150kV | 5A10 DIAMETER #10 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 1 - DIAMETER #10 | 5A10 | 150kV
209 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0019 - 5AB1 DIAMETER #1 150kV | 5AB1 DIAMETER #1 150kV | TRS-3413-073.073-B0019 - 5AB1 DIAMETER #1 150kV | 5AB1 DIAMETER #1 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #1 | 5AB1 | 150kV
210 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0020 - 5AB2 DIAMETER #2 150kV | 5AB2 DIAMETER #2 150kV | TRS-3413-073.073-B0020 - 5AB2 DIAMETER #2 150kV | 5AB2 DIAMETER #2 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #2 | 5AB2 | 150kV
211 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0021 - 5AB3 DIAMETER #3 150kV | 5AB3 DIAMETER #3 150kV | TRS-3413-073.073-B0021 - 5AB3 DIAMETER #3 150kV | 5AB3 DIAMETER #3 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #3 | 5AB3 | 150kV
212 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0022 - 5AB4 DIAMETER #4 150kV | 5AB4 DIAMETER #4 150kV | TRS-3413-073.073-B0022 - 5AB4 DIAMETER #4 150kV | 5AB4 DIAMETER #4 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #4 | 5AB4 | 150kV
213 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0023 - 5AB5 DIAMETER #5 150kV | 5AB5 DIAMETER #5 150kV | TRS-3413-073.073-B0023 - 5AB5 DIAMETER #5 150kV | 5AB5 DIAMETER #5 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #5 | 5AB5 | 150kV
214 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0024 - 5AB6 DIAMETER #6 150kV | 5AB6 DIAMETER #6 150kV | TRS-3413-073.073-B0024 - 5AB6 DIAMETER #6 150kV | 5AB6 DIAMETER #6 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #6 | 5AB6 | 150kV
215 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0025 - 5AB7 DIAMETER #7 150kV | 5AB7 DIAMETER #7 150kV | TRS-3413-073.073-B0025 - 5AB7 DIAMETER #7 150kV | 5AB7 DIAMETER #7 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #7 | 5AB7 | 150kV
216 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0026 - 5AB8 DIAMETER #8 150kV | 5AB8 DIAMETER #8 150kV | TRS-3413-073.073-B0026 - 5AB8 DIAMETER #8 150kV | 5AB8 DIAMETER #8 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #8 | 5AB8 | 150kV
217 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0027 - 5AB9 DIAMETER #9 150kV | 5AB9 DIAMETER #9 150kV | TRS-3413-073.073-B0027 - 5AB9 DIAMETER #9 150kV | 5AB9 DIAMETER #9 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #9 | 5AB9 | 150kV
218 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0028 - 5AB10 DIAMETER #10 150kV | 5AB10 DIAMETER #10 150kV | TRS-3413-073.073-B0028 - 5AB10 DIAMETER #10 150kV | 5AB10 DIAMETER #10 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #10 | 5AB10 | 150kV
219 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0048 - 5AB11 DIAMETER #11 150kV | 5AB11 DIAMETER #11 150kV | TRS-3413-073.073-B0048 - 5AB11 DIAMETER #11 150kV | 5AB11 DIAMETER #11 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #11 | 5AB11 | 150kV
220 | TRS-3413-073.073 - GI 150kV MUARAKARANG LAMA | TRS-3413-073.073-B0051 - 5AB12 DIAMETER #12 150kV | 5AB12 DIAMETER #12 150kV | TRS-3413-073.073-B0051 - 5AB12 DIAMETER #12 150kV | 5AB12 DIAMETER #12 150kV | ULTG DURIKOSAMBI | GI 150KV MUARAKARANG LAMA |  |  | CUT OFF 2 - DIAMETER #12 | 5AB12 | 150kV
221 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0002 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | TRF | #1 |  |  | 150/20kV
222 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0001 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | TRF | #2 |  |  | 150/20kV
223 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0019 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | TRF | #3 |  |  | 150/20kV
224 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0006 - PHT 150kV BALARAJA #1 | PHT 150kV BALARAJA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | PHT 150kV BALARAJA | #1 |  |  | 150kV
225 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0010 - PHT 150kV BALARAJA #2 | PHT 150kV BALARAJA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | PHT 150kV BALARAJA | #2 |  |  | 150kV
226 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0004 - PHT 150kV LAUTAN STEEL #1 | PHT 150kV LAUTAN STEEL #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | PHT 150kV LAUTAN STEEL | #1 |  |  | 150kV
227 | TRS-3413-139.139 - GI 150kV NEW BALARAJA | TRS-3413-139.139-B0011 - PHT 150kV LAUTAN STEEL #2 | PHT 150kV LAUTAN STEEL #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV NEW BALARAJA | PHT 150kV LAUTAN STEEL | #2 |  |  | 150kV
228 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0006 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | TRF | #1 |  |  | 150/20kV
229 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0007 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | TRF | #2 |  |  | 150/20kV
230 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0010 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | TRF | #3 |  |  | 150/20kV
231 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0014 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | TRF | #4 |  |  | 150/20kV
232 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0002 - PHT 150kV CIKUPA #1 | PHT 150kV CIKUPA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | PHT 150kV CIKUPA | #1 |  |  | 150kV
233 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0003 - PHT 150kV CIKUPA #2 | PHT 150kV CIKUPA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | PHT 150kV CIKUPA | #2 |  |  | 150kV
234 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0005 - PHT 150kV PASAR KEMIS BARU #1 | PHT 150kV PASAR KEMIS BARU #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | PHT 150kV PASAR KEMIS BARU | #1 |  |  | 150kV
235 | TRS-3413-049.049 - GI 150kV PASAR KEMIS | TRS-3413-049.049-B0004 - PHT 150kV PASAR KEMIS BARU #2 | PHT 150kV PASAR KEMIS BARU #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS | PHT 150kV PASAR KEMIS BARU | #2 |  |  | 150kV
236 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | TRF | #1 |  |  | 150/20kV
237 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | TRF | #2 |  |  | 150/20kV
238 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0010 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | TRF | #3 |  |  | 150/20kV
239 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0003 - PHT 150kV PASAR KEMIS #1 | PHT 150kV PASAR KEMIS #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | PHT 150kV PASAR KEMIS | #1 |  |  | 150kV
240 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0004 - PHT 150kV PASAR KEMIS #2 | PHT 150kV PASAR KEMIS #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | PHT 150kV PASAR KEMIS | #2 |  |  | 150kV
241 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0001 - PHT 150kV SEPATAN #1 | PHT 150kV SEPATAN #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | PHT 150kV SEPATAN | #1 |  |  | 150kV
242 | TRS-3413-058.058 - GI 150kV PASAR KEMIS BARU | TRS-3413-058.058-B0002 - PHT 150kV SEPATAN #2 | PHT 150kV SEPATAN #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV PASAR KEMIS BARU | PHT 150kV SEPATAN | #2 |  |  | 150kV
243 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0007 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | TRF | #1 |  |  | 150/20kV
244 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0012 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | TRF | #2 |  |  | 150/20kV
245 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0016 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | TRF | #3 |  |  | 150/20kV
246 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0017 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | TRF | #4 |  |  | 150/20kV
247 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0003 - PHT 150kV PASAR KEMIS BARU #1 | PHT 150kV PASAR KEMIS BARU #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | PHT 150kV PASAR KEMIS BARU | #1 |  |  | 150kV
248 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0004 - PHT 150kV PASAR KEMIS BARU #2 | PHT 150kV PASAR KEMIS BARU #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | PHT 150kV PASAR KEMIS BARU | #2 |  |  | 150kV
249 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0005 - PHT 150kV TELUK NAGA #1 | PHT 150kV TELUK NAGA #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | PHT 150kV TELUK NAGA | #1 |  |  | 150kV
250 | TRS-3413-053.053 - GI 150kV SEPATAN | TRS-3413-053.053-B0006 - PHT 150kV TELUK NAGA #2 | PHT 150kV TELUK NAGA #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV SEPATAN | PHT 150kV TELUK NAGA | #2 |  |  | 150kV
251 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0003 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | TRF | #1 |  |  | 150/20kV
252 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0004 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | TRF | #2 |  |  | 150/20kV
253 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0005 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | TRF | #3 |  |  | 150/20kV
254 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0009 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | TRF | #4 |  |  | 150/20kV
255 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0017 - TRF #5 150/20kV | TRF #5 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | TRF | #5 |  |  | 150/20kV
256 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0013 - PHT 150kV CENGKARENG #1 | PHT 150kV CENGKARENG #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | PHT 150kV CENGKARENG | #1 |  |  | 150kV
257 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0014 - PHT 150kV CENGKARENG #2 | PHT 150kV CENGKARENG #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | PHT 150kV CENGKARENG | #2 |  |  | 150kV
258 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0016 - PHT 150kV JATAKE #1 | PHT 150kV JATAKE #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | PHT 150kV JATAKE | #1 |  |  | 150kV
259 | TRS-3413-057.057 - GI 150kV TANGERANG | TRS-3413-057.057-B0015 - PHT 150kV JATAKE #2 | PHT 150kV JATAKE #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG | PHT 150kV JATAKE | #2 |  |  | 150kV
260 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | TRF | #1 |  |  | 150/20kV
261 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | TRF | #2 |  |  | 150/20kV
262 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0006 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | TRF | #3 |  |  | 150/20kV
263 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0014 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | TRF | #4 |  |  | 150/20kV
264 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0004 - PHT 150kV CENGKARENG BARU #1 | PHT 150kV CENGKARENG BARU #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #1 |  |  | 150kV
265 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0007 - PHT 150kV CENGKARENG BARU #2 | PHT 150kV CENGKARENG BARU #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | PHT 150kV CENGKARENG BARU | #2 |  |  | 150kV
266 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0001 - PHT 150kV LONTAR #1 | PHT 150kV LONTAR #1 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | PHT 150kV LONTAR | #1 |  |  | 150kV
267 | TRS-3413-061.061 - GI 150kV TANGERANG BARU | TRS-3413-061.061-B0013 - PHT 150kV LONTAR #2 | PHT 150kV LONTAR #2 | #N/A | 150kV | ULTG TANGKOT | GI 150KV TANGERANG BARU | PHT 150kV LONTAR | #2 |  |  | 150kV
268 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0002 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | TRF | #1 |  |  | 150/20kV
269 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0003 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | TRF | #2 |  |  | 150/20kV
270 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0013 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | TRF | #3 |  |  | 150/20kV
271 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0015 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | TRF | #4 |  |  | 150/20kV
272 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0010 - PHT 150kV LONTAR #1 | PHT 150kV LONTAR #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | PHT 150kV LONTAR | #1 |  |  | 150kV
273 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0011 - PHT 150kV LONTAR #2 | PHT 150kV LONTAR #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | PHT 150kV LONTAR | #2 |  |  | 150kV
274 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0009 - PHT 150kV SEPATAN #1 | PHT 150kV SEPATAN #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | PHT 150kV SEPATAN | #1 |  |  | 150kV
275 | TRS-3413-050.050 - GI 150kV TELUK NAGA | TRS-3413-050.050-B0001 - PHT 150kV SEPATAN #2 | PHT 150kV SEPATAN #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV TELUK NAGA | PHT 150kV SEPATAN | #2 |  |  | 150kV
276 | TRS-3413-052.052 - GI 150kV TIGARAKSA | TRS-3413-052.052-B0005 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TIGARAKSA | TRF | #1 |  |  | 150/20kV
277 | TRS-3413-052.052 - GI 150kV TIGARAKSA | TRS-3413-052.052-B0006 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TIGARAKSA | TRF | #2 |  |  | 150/20kV
278 | TRS-3413-052.052 - GI 150kV TIGARAKSA | TRS-3413-052.052-B0010 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TIGARAKSA | TRF | #3 |  |  | 150/20kV
279 | TRS-3413-052.052 - GI 150kV TIGARAKSA | TRS-3413-052.052-B0013 - TRF #4 150/20kV | TRF #4 150/20kV | #N/A | 150kV | ULTG CIKUPA | GI 150KV TIGARAKSA | TRF | #4 |  |  | 150/20kV
280 | TRS-3413-052.052 - GI 150kV TIGARAKSA | TRS-3413-052.052-B0003 - PHT 150kV CITRA HABITAT #1 | PHT 150kV CITRA HABITAT #1 | #N/A | 150kV | ULTG CIKUPA | GI 150KV TIGARAKSA | PHT 150kV CITRA HABITAT | #1 |  |  | 150kV
281 | TRS-3413-052.052 - GI 150kV TIGARAKSA | TRS-3413-052.052-B0004 - PHT 150kV CITRA HABITAT #2 | PHT 150kV CITRA HABITAT #2 | #N/A | 150kV | ULTG CIKUPA | GI 150KV TIGARAKSA | PHT 150kV CITRA HABITAT | #2 |  |  | 150kV
282 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0001 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | TRF | #1 |  |  | 150/20kV
283 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | TRF | #2 |  |  | 150/20kV
284 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0003 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | TRF | #3 |  |  | 150/20kV
285 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0007 - PHT 150kV CILEDUG #1 | PHT 150kV CILEDUG #1 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG | #1 |  |  | 150kV
286 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0012 - PHT 150kV CILEDUG #2 | PHT 150kV CILEDUG #2 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | PHT 150kV CILEDUG | #2 |  |  | 150kV
287 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-532.532-B0013 - PHT 150kV SUMMARECON GADING SERPONG #1 | PHT 150kV SUMMARECON GADING SERPONG #1 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG | #1 |  |  | 150kV
288 | TRS-3413-532.532 - GIS 150kV ALAM SUTERA | TRS-3413-DUM.000-B0020 - PHT 150kV SUMMARECON GADING SERPONG #2 | PHT 150kV SUMMARECON GADING SERPONG #2 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV ALAM SUTERA | PHT 150kV SUMMARECON GADING SERPONG | #2 |  |  | 150kV
289 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | TRF | #1 |  |  | 150/20kV
290 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | TRF | #2 |  |  | 150/20kV
291 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0010 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | TRF | #3 |  |  | 150/20kV
292 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0003 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI | #1 |  |  | 150kV
293 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0004 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | PHT 150kV DURIKOSAMBI | #2 |  |  | 150kV
294 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0001 - PHT 150kV PANTAI INDAH KAPUK #1 | PHT 150kV PANTAI INDAH KAPUK #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK | #1 |  |  | 150kV
295 | TRS-3413-193.193 - GIS 150kV DAAN MOGOT | TRS-3413-193.193-B0002 - PHT 150kV PANTAI INDAH KAPUK #2 | PHT 150kV PANTAI INDAH KAPUK #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV DAAN MOGOT | PHT 150kV PANTAI INDAH KAPUK | #2 |  |  | 150kV
296 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0007 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL | TRF | #1 |  |  | 150/20kV
297 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0008 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL | TRF | #2 |  |  | 150/20kV
298 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0006 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL | TRF | #3 |  |  | 150/20kV
299 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0004 - PHT 150kV GROGOL BARU #1 | PHT 150kV GROGOL BARU #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL | PHT 150kV GROGOL BARU | #1 |  |  | 150kV | 1600 / 1 | GEC Alsthom | MCTI | 422729L | Elektromekanik |  | 1 | 0,2 A | instant | instant | Definite
300 | TRS-3413-064.064 - GIS 150kV GROGOL | TRS-3413-064.064-B0005 - PHT 150kV GROGOL BARU #2 | PHT 150kV GROGOL BARU #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL | PHT 150kV GROGOL BARU | #2 |  |  | 150kV | 1600 / 1 | GEC Alsthom | MCTI | 422731L | Elektromekanik |  | 1 | 0,2 A | instant | instant | Definite
301 | [5 empty] | ULTG DURIKOSAMBI | GIS 150KV GROGOL | KOPEL BUS |  |  |  | 150kV | 2000 / 1 | GEC Alsthom | MCTI | 422737L | Elektromekanik |  | 1 | 0,2 A | instant | instant | Definite
302 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-10001 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | TRF | #1 |  |  | 150/20kV | [5 empty] | 2019
303 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-10002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | TRF | #2 |  |  | 150/20kV | [5 empty] | 2019
304 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0003 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI | #1 |  |  | 150kV | 2000 / 1 | Siemens |  | BM1804004748 | Numerik | 2019 | 1 | 0,2 A | instant | instant | Definite
305 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0004 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI | #2 |  |  | 150kV | 1600 / 1 | Siemens | 7VK87 | BM1804004748 | Numerik | 2019 | 1 | 0,2 A | instant | instant | Definite
306 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0001 - PHT 150kV GROGOL #1 | PHT 150kV GROGOL #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | PHT 150kV GROGOL | #1 |  |  | 150kV | [5 empty] | 2019
307 | TRS-3413-021.021 - GIS 150kV GROGOL BARU | TRS-3413-021.021-B0002 - PHT 150kV GROGOL #2 | PHT 150kV GROGOL #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | PHT 150kV GROGOL | #2 |  |  | 150kV | [5 empty] | 2019
308 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0003 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | TRF | #1 |  |  | 150/20kV
309 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0004 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | TRF | #2 |  |  | 150/20kV | 250 / 5 | Alstom | P14D | 35030424/03/20 | Numerik | 2021 | 5 | 5 A | 100 | 250 | Definite
310 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0005 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | TRF | #3 |  |  | 150/20kV | 250 / 5 | Alstom | P14D | 35030422/03/20 | Numerik | 2021 | 5 | 500 | 200 | 250 | Definite
311 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0007 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI | #1 |  |  | 150kV | 500 / 5 | ABB | REF 615E G | 1VHR91327611 | Numerik | 2021 | 5 | 100 | 100 | 250 | Definite
312 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0008 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | PHT 150kV DURIKOSAMBI | #2 |  |  | 150kV
313 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0006 - PHT 150kV KARET BARU #1 | PHT 150kV KARET BARU #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU | #1 |  |  | 150kV | 500 / 5 | ABB | REF 615 | 1VHR91327614 | Numerik | 2021 | 5 | 25 A | 100 | 250 | Definite
314 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | TRS-3413-063.063-B0011 - PHT 150kV KARET BARU #2 | PHT 150kV KARET BARU #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | PHT 150kV KARET BARU | #2 |  |  | 150kV | 500 / 5 | ABB | REF 615 | 1VHR91344410 | Numerik | 2021 | 5 | 25 A | 100 | 250 | Definite
315 | TRS-3413-063.063 - GIS 150kV KEBON JERUK | #N/A | KOPEL BUS | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEBON JERUK | KOPEL BUS |  |  |  | 150kV | 2000 / 5 | ABB | REF 615E G | 1VHR91331923 | Numerik | 2021 | 5 | 100 | 100 | 250 | Definite
316 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0012 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | TRF | #1 |  |  | 150/20kV
317 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | TRF | #2 |  |  | 150/20kV
318 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0017 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | TRF | #3 |  |  | 150/20kV
319 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0002 - PHT 150kV CILEDUG #1 | PHT 150kV CILEDUG #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV CILEDUG | #1 |  |  | 150kV
320 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0005 - PHT 150kV CILEDUG #2 | PHT 150kV CILEDUG #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV CILEDUG | #2 |  |  | 150kV
321 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0006 - PHT 150kV DURIKOSAMBI #1 | PHT 150kV DURIKOSAMBI #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI | #1 |  |  | 150kV
322 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0007 - PHT 150kV DURIKOSAMBI #2 | PHT 150kV DURIKOSAMBI #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV DURIKOSAMBI | #2 |  |  | 150kV
323 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0013 - PHT 150kV NEW SENAYAN #1 | PHT 150kV NEW SENAYAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN | #1 |  |  | 150kV
324 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0008 - PHT 150kV NEW SENAYAN #2 | PHT 150kV NEW SENAYAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV NEW SENAYAN | #2 |  |  | 150kV
325 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0018 - PHT 150kV PETUKANGAN #1 | PHT 150kV PETUKANGAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN | #1 |  |  | 150kV
326 | TRS-3413-059.059 - GIS 150kV KEMBANGAN | TRS-3413-059.059-B0019 - PHT 150kV PETUKANGAN #2 | PHT 150kV PETUKANGAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV KEMBANGAN | PHT 150kV PETUKANGAN | #2 |  |  | 150kV
327 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0014 - PHT 150kV TANGERANG BARU #1 | PHT 150kV TANGERANG BARU #1 | TRS-3413-144.144-B0002 - 5B2 DIAMETER #2 150kV | 5B2 DIAMETER #2 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU | #1 | CUT OFF 3 - DIAMETER #2 | 5B2 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100901001 | Numerik |  | 1 | 200 | 100 | 250 | DT
328 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0016 - PHT 150kV TANGERANG BARU #2 | PHT 150kV TANGERANG BARU #2 | TRS-3413-144.144-B0001 - 5B1 DIAMETER #1 150kV | 5B1 DIAMETER #1 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV TANGERANG BARU | #2 | CUT OFF 3 - DIAMETER #1 | 5B1 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900401 | Numerik |  | 1 | 200 | 100 | 250 | DT
329 | TRS-3413-144.144 - GIS 150kV LONTAR | #N/A | PHT 150kV DADAP #1 | TRS-3413-144.144-B0004 - 5B4 DIAMETER #4 150kV | 5B4 DIAMETER #4 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV DADAP | #1 | CUT OFF 3 - DIAMETER #4 | 5B4 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900701 | Numerik |  | 1 | 200 | 100 | 250 | DT
330 | TRS-3413-144.144 - GIS 150kV LONTAR | #N/A | PHT 150kV DADAP #2 | TRS-3413-144.144-B0003 - 5B3 DIAMETER #3 150kV | 5B3 DIAMETER #3 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV DADAP | #2 | CUT OFF 3 - DIAMETER #3 | 5B3 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900101 | Numerik |  | 1 | 200 | 100 | 250 | DT
331 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0005 - 5AB1 DIAMETER #1 150kV | 5AB1 DIAMETER #1 150kV | TRS-3413-144.144-B0005 - 5AB1 DIAMETER #1 150kV | 5AB1 DIAMETER #1 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #1 | 5AB1 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900801 | Numerik |  | 1 | 200 | 100 | 250 | DT
332 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0006 - 5AB2 DIAMETER #2 150kV | 5AB2 DIAMETER #2 150kV | TRS-3413-144.144-B0006 - 5AB2 DIAMETER #2 150kV | 5AB2 DIAMETER #2 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #2 | 5AB2 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900301 | Numerik |  | 1 | 200 | 100 | 250 | DT
333 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0007 - 5AB3 DIAMETER #3 150kV | 5AB3 DIAMETER #3 150kV | TRS-3413-144.144-B0007 - 5AB3 DIAMETER #3 150kV | 5AB3 DIAMETER #3 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #3 | 5AB3 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100901201 | Numerik |  | 1 | 200 | 100 | 250 | DT
334 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0008 - 5AB4 DIAMETER #4 150kV | 5AB4 DIAMETER #4 150kV | TRS-3413-144.144-B0008 - 5AB4 DIAMETER #4 150kV | 5AB4 DIAMETER #4 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #4 | 5AB4 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900201 | Numerik |  | 1 | 200 | 100 | 250 | DT
335 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0017 - 5A1 DIAMETER #1 150kV | 5A1 DIAMETER #1 150kV | TRS-3413-144.144-B0017 - 5A1 DIAMETER #1 150kV | 5A1 DIAMETER #1 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 1 - DIAMETER #1 | 5A1 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900901 | Numerik |  | 1 | 200 | 100 | 250 | DT
336 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0015 - 5A2 DIAMETER #2 150kV | 5A2 DIAMETER #2 150kV | TRS-3413-144.144-B0015 - 5A2 DIAMETER #2 150kV | 5A2 DIAMETER #2 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 1 - DIAMETER #2 | 5A2 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900901 | Numerik |  | 1 | 200 | 100 | 250 | DT
337 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0010 - 5A3 DIAMETER #3 150kV | 5A3 DIAMETER #3 150kV | TRS-3413-144.144-B0010 - 5A3 DIAMETER #3 150kV | 5A3 DIAMETER #3 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 1 - DIAMETER #3 | 5A3 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900501 | Numerik |  | 1 | 200 | 100 | 250 | DT
338 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-144.144-B0018 - 5A4 DIAMETER #4 150kV | 5A4 DIAMETER #4 150kV | TRS-3413-144.144-B0018 - 5A4 DIAMETER #4 150kV | 5A4 DIAMETER #4 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 1 - DIAMETER #4 | 5A4 | 150kV | 3200 / 1 | NR | RCS-921 | 7430100900601 | Numerik |  | 1 | 200 | 100 | 250 | DT
[6 empty] | ULTG CIKUPA | GIS 150KV LONTAR |  |  | SEKSI BUS A | 5A5 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 619305F | Numerik |  | 1 | 200 | 100 | 250 | DT
[6 empty] | ULTG CIKUPA | GIS 150KV LONTAR |  |  | SEKSI BUS B | 5B5 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 614378F | Numerik |  | 1 | 200 | 100 | 250 | DT
339 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0036 - 5B6 DIAMETER #6 150kV | 5B6 DIAMETER #6 150kV | TRS-3413-DUM.000-B0036 - 5B6 DIAMETER #6 150kV | 5B6 DIAMETER #6 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA | #1 | CUT OFF 3 - DIAMETER #6 | 5B6 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 614377F | Numerik |  | 1 | 200 | 100 | 250 | DT
340 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0038 - 5B7 DIAMETER #7 150kV | 5B7 DIAMETER #7 150kV | TRS-3413-DUM.000-B0038 - 5B7 DIAMETER #7 150kV | 5B7 DIAMETER #7 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV SINDANG JAYA | #2 | CUT OFF 3 - DIAMETER #7 | 5B7 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 619303F | Numerik |  | 1 | 200 | 100 | 250 | DT
341 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0033 - 5B8 DIAMETER #8 150kV | 5B8 DIAMETER #8 150kV | TRS-3413-DUM.000-B0033 - 5B8 DIAMETER #8 150kV | 5B8 DIAMETER #8 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV CIKUPA (FUTURE) | #1 | CUT OFF 3 - DIAMETER #8 | 5B8 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 619308F | Numerik |  | 1 | 200 | 100 | 250 | DT
342 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0031 - 5B9 DIAMETER #9 150kV | 5B9 DIAMETER #9 150kV | TRS-3413-DUM.000-B0031 - 5B9 DIAMETER #9 150kV | 5B9 DIAMETER #9 150kV | ULTG CIKUPA | GIS 150KV LONTAR | PHT 150kV CIKUPA (FUTURE) | #2 | CUT OFF 3 - DIAMETER #9 | 5B9 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 619304F | Numerik |  | 1 | 200 | 100 | 250 | DT
343 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0035 - 5AB6 DIAMETER #6 150kV | 5AB6 DIAMETER #6 150kV | TRS-3413-DUM.000-B0035 - 5AB6 DIAMETER #6 150kV | 5AB6 DIAMETER #6 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #6 | 5AB6 | 150kV | 4000 /1 | SCHNEIDER | P841 | 614379F | Numerik |  | 1 | 200 | 100 | 250 | DT
344 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0037 - 5AB7 DIAMETER #7 150kV | 5AB7 DIAMETER #7 150kV | TRS-3413-DUM.000-B0037 - 5AB7 DIAMETER #7 150kV | 5AB7 DIAMETER #7 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #7 | 5AB7 | 150kV | 4000 /1 | SCHNEIDER | P841 | 619309F | Numerik |  | 1 | 200 | 100 | 250 | DT
345 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0032 - 5AB8 DIAMETER #8 150kV | 5AB8 DIAMETER #8 150kV | TRS-3413-DUM.000-B0032 - 5AB8 DIAMETER #8 150kV | 5AB8 DIAMETER #8 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #8 | 5AB8 | 150kV | 4000 /1 | SCHNEIDER | P841 | 619302F | Numerik |  | 1 | 200 | 100 | 250 | DT
346 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0030 - 5AB9 DIAMETER #9 150kV | 5AB9 DIAMETER #9 150kV | TRS-3413-DUM.000-B0030 - 5AB9 DIAMETER #9 150kV | 5AB9 DIAMETER #9 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 2 - DIAMETER #9 | 5AB9 | 150kV | 4000 /1 | SCHNEIDER | P841 | 614380F | Numerik |  | 1 | 200 | 100 | 250 | DT
347 | TRS-3413-144.144 - GIS 150kV LONTAR | TRS-3413-DUM.000-B0034 - 5A6 DIAMETER #6 150kV | 5A6 DIAMETER #6 150kV | TRS-3413-DUM.000-B0034 - 5A6 DIAMETER #6 150kV | 5A6 DIAMETER #6 150kV | ULTG CIKUPA | GIS 150KV LONTAR |  |  | CUT OFF 1 - DIAMETER #6 | 5A6 | 150kV | 4000 / 1 | SCHNEIDER | P841 | 614381F | Numerik |  | 1 | 200 | 100 | 250 | DT
347 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0011 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | TRF | #1 |  |  | 150/20kV
348 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0008 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | TRF | #2 |  |  | 150/20kV | 1600 / 1 | Areva | MiCom P821 | 60788 | Numerik |  | 1 | 0,2 A | instant | instant | Definite
349 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0003 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | TRF | #3 |  |  | 150/20kV
350 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0007 - PHT 150kV KEMBANGAN #1 | PHT 150kV KEMBANGAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN | #1 |  |  | 150kV
351 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-136.136-B0005 - PHT 150kV KEMBANGAN #2 | PHT 150kV KEMBANGAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | PHT 150kV KEMBANGAN | #2 |  |  | 150kV
352 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-DUM.000-B0039 - PHT 150kV SENAYAN #1 | PHT 150kV SENAYAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN | #1 |  |  | 150kV
353 | TRS-3413-136.136 - GIS 150kV NEW SENAYAN | TRS-3413-DUM.000-B0040 - PHT 150kV SENAYAN #2 | PHT 150kV SENAYAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV NEW SENAYAN | PHT 150kV SENAYAN | #2 |  |  | 150kV
354 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0007 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV PANTAI INDAH KAPUK | TRF | #2 |  |  | 150/20kV | 1600 / 1 |  |  | 607788 |  |  | 1 | 0,2 A | instant | instant | Definite
355 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0009 - TRF #3 150/20kV | TRF #3 150/20kV | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV PANTAI INDAH KAPUK | TRF | #3 |  |  | 150/20kV
356 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0003 - PHT 150kV DAAN MOGOT #1 | PHT 150kV DAAN MOGOT #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT | #1 |  |  | 150kV
357 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0004 - PHT 150kV DAAN MOGOT #2 | PHT 150kV DAAN MOGOT #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV DAAN MOGOT | #2 |  |  | 150kV
358 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0001 - PHT 150kV MUARAKARANG BARU #1 | PHT 150kV MUARAKARANG BARU #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV MUARAKARANG BARU | #1 |  |  | 150kV
359 | TRS-3413-538.538 - GIS 150kV PANTAI INDAH KAPUK | TRS-3413-538.538-B0002 - PHT 150kV MUARAKARANG BARU #2 | PHT 150kV MUARAKARANG BARU #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV PANTAI INDAH KAPUK | PHT 150kV MUARAKARANG BARU | #2 |  |  | 150kV
348 | TRS-3413-186.186 - GIS 150kV SPINMILL | TRS-3413-186.186-B0008 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SPINMILL | TRF | #1 |  |  | 150/20kV | 300/1 | SIEMENS | 7VK87 | BM1704007797 | Numerik | 2018 | 1 | 300 | 150 | 250 | DT
349 | TRS-3413-186.186 - GIS 150kV SPINMILL | TRS-3413-186.186-B0009 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SPINMILL | TRF | #2 |  |  | 150/20kV | 300/1 | SIEMENS | 7VK87 | BM1704007800 | Numerik | 2018 | 1 | 300 | 100 | 250 | DT
350 | TRS-3413-186.186 - GIS 150kV SPINMILL | TRS-3413-186.186-B0004 - PHT 150kV LAUTAN STEEL #1 | PHT 150kV LAUTAN STEEL #1 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SPINMILL | PHT 150kV LAUTAN STEEL | #1 |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1704007794 | Numerik | 2018 | 1 | 300 | 100 | 250 | DT
351 | TRS-3413-186.186 - GIS 150kV SPINMILL | TRS-3413-186.186-B0005 - PHT 150kV LAUTAN STEEL #2 | PHT 150kV LAUTAN STEEL #2 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SPINMILL | PHT 150kV LAUTAN STEEL | #2 |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1704007791 | Numerik | 2018 | 1 | 300 | 100 | 250 | DT
352 | TRS-3413-186.186 - GIS 150kV SPINMILL | TRS-3413-186.186-B0006 - PHT 150kV MILENIUM #1 | PHT 150kV MILENIUM #1 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SPINMILL | PHT 150kV MILENIUM | #1 |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1705000805 | Numerik | 2018 | 1 | 300 | 100 | 250 | DT
353 | TRS-3413-186.186 - GIS 150kV SPINMILL | TRS-3413-186.186-B0007 - PHT 150kV MILENIUM #2 | PHT 150kV MILENIUM #2 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SPINMILL | PHT 150kV MILENIUM | #2 |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1704007788 | Numerik | 2018 | 1 | 300 | 100 | 250 | DT
354 | [5 empty] | ULTG CIKUPA | GIS 150KV SPINMILL | KOPEL BUS |  |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1704007803 | Numerik | 2018 | 1 | 300 | 100 | 250 | DT
367 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-10001 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV SUMMARECON GADING SERPONG | TRF | #1 |  |  | 150/20kV
368 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-10002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG TANGKOT | GIS 150KV SUMMARECON GADING SERPONG | TRF | #2 |  |  | 150/20kV
369 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20003 - PHT 150kV ALAM SUTERA #1 | PHT 150kV ALAM SUTERA #1 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA | #1 |  |  | 150kV
370 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20004 - PHT 150kV ALAM SUTERA #2 | PHT 150kV ALAM SUTERA #2 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV ALAM SUTERA | #2 |  |  | 150kV
371 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20001 - PHT 150kV CURUG #1 | PHT 150kV CURUG #1 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG | #1 |  |  | 150kV
372 | TRS-3413-019.019 - GIS 150kV SUMMARECON GADING SERPONG | TRS-3413-019.019-20002 - PHT 150kV CURUG #2 | PHT 150kV CURUG #2 | #N/A | 150kV | ULTG TANGKOT | GIS 150KV SUMMARECON GADING SERPONG | PHT 150kV CURUG | #2 |  |  | 150kV
355 | TRS-3413-020.020 - GIS 150kV SUVARNA SUTERA | TRS-3413-020.020-10001 - TRF #1 150/20kV | TRF #1 150/20kV | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | TRF | #1 |  |  | 150/20kV | 300/1 | SIEMENS | 7VK87 | BM1802004679 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
356 | TRS-3413-020.020 - GIS 150kV SUVARNA SUTERA | TRS-3413-020.020-10002 - TRF #2 150/20kV | TRF #2 150/20kV | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | TRF | #2 |  |  | 150/20kV | 300/1 | SIEMENS | 7VK87 | BM1802004664 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
357 | TRS-3413-020.020 - GIS 150kV SUVARNA SUTERA | #N/A | PHT 150kV SINDANG JAYA #1 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | PHT 150kV SINDANG JAYA | #1 |  |  | 150kV | 4000 / 1 | SIEMENS | 7VK87 | BM1802004670 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
358 | TRS-3413-020.020 - GIS 150kV SUVARNA SUTERA | #N/A | PHT 150kV SINDANG JAYA #2 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | PHT 150kV SINDANG JAYA | #2 |  |  | 150kV | 4000 / 1 | SIEMENS | 7VK87 | BM1802004820 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
359 | TRS-3413-020.020 - GIS 150kV SUVARNA SUTERA | TRS-3413-020.020-20003 - PHT 150kV CIKUPA #1 | PHT 150kV CIKUPA #1 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | PHT 150kV CIKUPA | #1 |  |  | 150kV | 4000 / 1 | SIEMENS | 7VK87 | BM1802004676 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
360 | TRS-3413-020.020 - GIS 150kV SUVARNA SUTERA | TRS-3413-020.020-20004 - PHT 150kV CIKUPA #2 | PHT 150kV CIKUPA #2 | #N/A | 150kV | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | PHT 150kV CIKUPA | #2 |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1802004667 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
361 | [5 empty] | ULTG CIKUPA | GIS 150KV SUVARNA SUTERA | KOPEL BUS |  |  |  | 150kV | 767011 | SIEMENS | 7VK87 | BM1802004673 | Numerik | 2019 | 1 | 200 | 100 | 250 | DT
380 | #N/A | #N/A | TRF #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV TOMANG | TRF | #1 |  |  | 150/20kV | 300 / 1 | Schneider | MiCom P841 |  | Numerik | 2021 | 1 | 200 | 100 | 250
381 | #N/A | #N/A | TRF #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV TOMANG | TRF | #2 |  |  | 150/20kV | 300 / 1 | Schneider | MiCom P841 |  | Numerik | 2021 | 1 | 200 | 100 | 250
382 | #N/A | #N/A | PHT 150kV GROGOL #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV TOMANG | PHT 150kV GROGOL | #1 |  |  | 150kV | 2000 / 1 | Schneider | MiCom P841 |  | Numerik | 2021 | 1 | 200 | 100 | 250
383 | #N/A | #N/A | PHT 150kV GROGOL #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV TOMANG | PHT 150kV GROGOL | #2 |  |  | 150kV | 2000 / 1 | Schneider | MiCom P841 |  | Numerik | 2021 | 1 | 200 | 100 | 250
384 | #N/A | #N/A | KOPEL BUS | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV TOMANG | KOPEL BUS |  |  |  | 150kV | 4000 / 1 | Schneider | MiCom P841 |  | Numerik | 2021 | 1 | 200 | 100 | 250
385 | #N/A | #N/A | TRF #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV ULUJAMI | TRF | #1 |  |  | 150/20kV | 2000 / 1 | GE Alstom | MiCom P14D | 34731621/03/19 | Numerik | 2021 | 1 | 200 | 150 | 250
386 | #N/A | #N/A | TRF #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV ULUJAMI | TRF | #2 |  |  | 150/20kV | 2000 / 1 | GE Alstom | MiCom P14D | 34731615/03/19 | Numerik | 2021 | 1 | 200 | 150 | 250
387 | #N/A | #N/A | PHT 150kV NEW SENAYAN #1 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN | #1 |  |  | 150kV | 2000 / 1 | GE Alstom | MiCom P14D | 34731616/03/19 | Numerik | 2021 | 1 | 200 | 150 | 250
388 | #N/A | #N/A | PHT 150kV NEW SENAYAN #2 | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV ULUJAMI | PHT 150kV NEW SENAYAN | #2 |  |  | 150kV | 2000 / 1 | GE Alstom | MiCom P14D | 34731618/03/19 | Numerik | 2021 | 1 | 200 | 150 | 250
389 | #N/A | #N/A | KOPEL BUS | #N/A | 150kV | ULTG DURIKOSAMBI | GIS 150KV ULUJAMI | KOPEL BUS |  |  |  | 150kV | 2000 / 1 | GE Alstom | MiCom P14D | 34731619/03/19 | Numerik | 2021 | 1 | 200 | 150 | 250

## CCP
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT DURIKOSAMBI
NO | GI / GIS | BAY | BAY | ULTG | GI / GIS | BAY | SIRKIT | DIAMETER | kV | RATIO CT | CCP 1 | [10 empty] | RATIO CT | CCP 2 | [10 empty] | KET
[11 empty] | MERK | Type | NO. SERIE | JENIS RELE | TH OPERASI | SETTING | [6 empty] | MERK | TYPE | NO. SERIE | JENIS RELE | TH OPERASI | SETTING
[16 empty] | In | Iset (A) | Is1 (pu) | Is2 (pu) | time | karakteristik | [6 empty] | In | Iset (A) | Is1 (pu) | Is2 (pu) | time | karakteristik
1 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #1 | CUT OFF 1 - DIAMETER 1 | 500/150kV | 2000 / 1 | Areva | MCAG 34 | 10025276/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025277/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
2 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0002 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #2 | CUT OFF 1 - DIAMETER 2 | 500/150kV | 2000 / 1 | Areva | MCAG 34 | 10025273/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025318/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
3 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0029 - IBT #3 500/150kV (HV) | IBT #3 500/150kV (HV) | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #3 | CUT OFF 1 - DIAMETER 5 | 500/150kV | 1000 / 1 | Siemens | 7UT61 | BF1201067964 | Numerik |  | 1 |  | 0.2 | 8 | instant | DT | 2000 / 1 | Siemens | 7UT61 | BF1201067961 | Numerik |  | 1 |  | 0.2 | 8 | instant | DT
4 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0030 - IBT #4 500/150kV (HV) | IBT #4 500/150kV (HV) | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #4 | CUT OFF 1 - DIAMETER 6 | 500/150kV | 2000 / 1 | Alstom | MiCom P643 | 32677515/09/13 | Numerik |  | 1 |  | 0.2 | 8 | instant | DT | 2000 / 1 | Alstom | MiCom P643 | 32677514/09/13 | Numerik |  | 1 |  | 0.2 | 8 | instant | DT
5 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0015 - PHT 500kV JAWA 7 #1 | PHT 500kV JAWA 7 #1 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV JAWA 7 | #1 | CUT OFF 3 - DIAMETER 2 | 500kV | 2000 / 1 | Areva | MCAG 34 | 10025274/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025278/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
6 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0014 - PHT 500kV JAWA 7 #2 | PHT 500kV JAWA 7 #2 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV JAWA 7 | #2 | CUT OFF 3 - DIAMETER 1 | 500kV | 2000 / 1 | Areva | MCAG 34 | 10025312/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025321/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
7 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0004 - PHT 500kV LENGKONG #1 | PHT 500kV LENGKONG #1 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV LENGKONG | #1 | CUT OFF 1 - DIAMETER 3 | 500kV | 2000 / 1 | Areva | MCAG 34 | 10025315/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025275/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
8 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0013 - PHT 500kV LENGKONG #2 | PHT 500kV LENGKONG #2 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV LENGKONG | #2 | CUT OFF 1 - DIAMETER 4 | 500kV | 2000 / 1 | Areva | MCAG 34 | 10025316/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025313/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
9 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0005 - PHT 500kV SURALAYA #1 | PHT 500kV SURALAYA #1 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV SURALAYA | #1 | CUT OFF 3 - DIAMETER 3 | 500kV | 2000 / 1 | Areva | MCAG 34 | 10025279/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025317/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
10 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0012 - PHT 500kV SURALAYA #2 | PHT 500kV SURALAYA #2 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV SURALAYA | #2 | CUT OFF 3 - DIAMETER 4 | 500kV | 2000 / 1 | Areva | MCAG 34 | 10025311/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT | 2000 / 1 | Areva | MCAG 34 | 10025320/08/07 | Elektromekanik |  | 1 | 0.2 |  |  | instant | DT
11 | TRS-3413-008.008 - GITET 500kV BALARAJA | #N/A | PHT 500kV KEMBANGAN (FUTURE) #1 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV KEMBANGAN (FUTURE) | #1 | CUT OFF 3 - DIAMETER 5 | 500kV | 2000 / 1 | SIEMENS | 7UT86 | BM1803009884 | Numerik |  | 1 |  | 0.3 | - | instant | DT | 2000 / 1 | Schneider | P645 | 647328F | Numerik |  | 1 |  | 0.3 | 2 | instant | DT
12 | TRS-3413-008.008 - GITET 500kV BALARAJA | #N/A | PHT 500kV KEMBANGAN (FUTURE) #2 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV KEMBANGAN (FUTURE) | #2 | CUT OFF 3 - DIAMETER 6 | 500kV | 2000 / 1 | SIEMENS | 7UT86 | BM1803009887 | Numerik |  | 1 |  | 0.3 | - | instant | DT | 2000 / 1 | Schneider | P645 | 647329F | Numerik |  | 1 |  | 0.3 | 2 | instant | DT
13 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV TANGERANG BARU | #1 | CUT OFF 3 - DIAMETER #2 | 150 kV
14 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV TANGERANG BARU | #2 | CUT OFF 3 - DIAMETER #1 | 150 kV
15 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV DADAP | #1 | CUT OFF 3 - DIAMETER #4 | 150 kV
16 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV DADAP | #2 | CUT OFF 3 - DIAMETER #3 | 150 kV
17 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV SINDANG JAYA | #1 | CUT OFF 3 - DIAMETER #6 | 150 kV | 4000 / 1 | SCHNEIDER | P841 | 620640F | Numerik |  | 1 |  | 0.3 | 2 | Instan | DT
18 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV SINDANG JAYA | #2 | CUT OFF 3 - DIAMETER #7 | 150 kV | 4000 / 1 | SCHNEIDER | P841 | 620642F | Numerik |  | 1 |  | 0.3 | 2 | Instan | DT
19 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV CIKUPA (FUTURE) | #1 | CUT OFF 3 - DIAMETER #8 | 150 kV | 4000 / 1 | SCHNEIDER | P841 | 620645F | Numerik |  | 1 |  | 0.3 | 2 | Instan | DT
20 |  |  |  | ULTG CIKUPA | GIS LONTAR | PHT 150kV CIKUPA (FUTURE) | #2 | CUT OFF 3 - DIAMETER #9 | 150 kV | 4000 / 1 | SCHNEIDER | P841 | 620644F | Numerik |  | 1 |  | 0.3 | 2 | Instan | DT
21 |  |  |  | ULTG CIKUPA | GIS LONTAR |  |  | CUT OFF 1 - DIAMETER #1 | 150 kV
22 |  |  |  | ULTG CIKUPA | GIS LONTAR |  |  | CUT OFF 1 - DIAMETER #2 | 150 kV
23 |  |  |  | ULTG CIKUPA | GIS LONTAR |  |  | CUT OFF 1 - DIAMETER #3 | 150 kV
24 |  |  |  | ULTG CIKUPA | GIS LONTAR |  |  | CUT OFF 1 - DIAMETER #4 | 150 kV
25 |  |  |  | ULTG CIKUPA | GIS LONTAR |  |  | CUT OFF 1 - DIAMETER #6 | 150 kV | 4000 / 1 | SCHNEIDER | P841 | 620639F | Numerik |  | 1 |  | 0.3 | 2 | Instan | DT
26 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0001 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT | #1 | CUT OFF 3 - DIAMETER 1 | 500/150kV
27 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0004 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT | #2 | CUT OFF 3 - DIAMETER 2 | 500/150kV
28 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0082 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL | #1 | CUT OFF 1 - DIAMETER 4 | 500kV
29 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0075 - PHT 500kV KEMBANGAN #2 | PHT 500kV KEMBANGAN #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN | #2 | CUT OFF 1 - DIAMETER 3 | 500kV
30 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | IBT (FUTURE) #3 500/150kV (HV) | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT (FUTURE) | #3 | CUT OFF 3 - DIAMETER 3 | 500/150kV
31 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | IBT (FUTURE) #4 500/150kV (HV) | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT (FUTURE) | #4 | CUT OFF 3 - DIAMETER 4 | 500/150kV
32 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | PHT 500kV MUARAKARANG (FUTURE) #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG (FUTURE) | #1 | CUT OFF 1 - DIAMETER 2 | 500kV
33 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | PHT 500kV MUARAKARANG (FUTURE) #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG (FUTURE) | #2 | CUT OFF 1 - DIAMETER 1 | 500kV
34 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 | CUT OFF 1 - DIAMETER 1 | 500/150kV | 1000 / 1 | GEC Alsthom | MCAG 14 | 637080B | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI | 1000 / 1 | GEC Alsthom | MCAG 14 | 637079B | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI
35 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0005 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #2 | CUT OFF 1 - DIAMETER 2 | 500/150kV | 1000 / 1 | Areva | MCAG 34 | 637077B | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI | 1000 / 1 | Areva | MCAG 34 | 637078B | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI
36 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-DUM.000-B0072 - PHT 500kV DURIKOSAMBI #1 | PHT 500kV DURIKOSAMBI #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #1 | CUT OFF 3 - DIAMETER 3 | 500kV
37 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0018 - PHT 500kV DURIKOSAMBI #2 | PHT 500kV DURIKOSAMBI #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #2 | CUT OFF 3 - DIAMETER 4 | 500kV
38 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0007 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #1 | CUT OFF 3 - DIAMETER 1 | 500kV | 2000 / 1 | GEC Alsthom | MCAG |  | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI | 2000 / 1 | GEC Alsthom | MCAG |  | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI
39 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0008 - PHT 500kV GANDUL #2 | PHT 500kV GANDUL #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #2 | CUT OFF 3 - DIAMETER 2 | 500kV | 2000 / 1 | GEC Alsthom | MCAG |  | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI | 2000 / 1 | GEC Alsthom | MCAG |  | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI
40 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | PHT 500kV BALARAJA (FUTURE) #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA (FUTURE) | #1 | CUT OFF 1 - DIAMETER 4 | 500kV
41 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | PHT 500kV BALARAJA (FUTURE) #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV BALARAJA (FUTURE) | #2 | CUT OFF 1 - DIAMETER 3 | 500kV
42 |  |  |  | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI | #1 |  | 150kV | 2000 / 1 | Siemens | 7UT86 | BM1804005463 | Numerik | 2019 | 1 | 0.3 |  |  | instant | SI
43 |  |  |  | ULTG DURIKOSAMBI | GIS 150KV GROGOL BARU | PHT 150kV DURIKOSAMBI | #2 |  | 150kV | 2000 / 1 | Siemens | 7UT86 | BM1804005463 | Numerik | 2019 | 1 | 0.7 |  |  | instant | SI
44 |  |  |  | ULTG DURIKOSAMBI | GIS 150KV GROGOL | PHT 150kV GROGOL BARU | #1 |  | 150kV | 1600 / 1 | GEC Alsthom | MCAG 34 | 637080B | Elektromekanik |  | 1 | 0.2 |  |  | instant | SI

## SZP
UNIT INDUK TRANSMISI JAWA BAGIAN BARAT
UPT GISTET 500KV DURIKOSAMBI
NO | GI / GIS | BAY | BAY | DIAMETER | DIAMETER | DIAMETER | ULTG | GI / GIS | BAY | SIRKIT | DIAMETER | PMT | kV | RATIO CT | SZP | [8 empty] | KET
[15 empty] | MERK | Type | NO. SERIE | JENIS RELE | TH OPERASI | SETTING
[20 empty] | In | Iset (A) | time | karakteristik
1 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-008.008-B0008 - 7A1 DIAMETER #1 500kV | 7A1 DIAMETER #1 500kV | DIAMETER #1 | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7A1 | 500/150kV | 2000 / 1 | Areva | MiCom P821 | 3307182 | Numerik |  | 1 | 0.2 | 0.07
2 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0002 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | TRS-3413-008.008-B0018 - 7A2 DIAMETER #2 500kV | 7A2 DIAMETER #2 500kV | DIAMETER #2 | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #2 | CUT OFF 1 - DIAMETER #2 | 7A2 | 500/150kV | 2000 / 1 | Areva | MiCom P821 | 3307172 | Numerik |  | 1 | 0.2 | 0.07
3 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0029 - IBT #3 500/150kV (HV) | IBT #3 500/150kV (HV) | TRS-3413-008.008-B0023 - 7A5 DIAMETER #5 500kV | 7A5 DIAMETER #5 500kV | DIAMETER #5 | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #3 | CUT OFF 1 - DIAMETER #5 | 7A5 | 500/150kV | 1000 / 1 | Siemens | 7VK61 | BF1201064272 | Numerik |  | 1 | 0.2 | 0.07
4 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0030 - IBT #4 500/150kV (HV) | IBT #4 500/150kV (HV) | TRS-3413-008.008-B0026 - 7A6 DIAMETER #6 500kV | 7A6 DIAMETER #6 500kV | DIAMETER #6 | ULTG CIKUPA | GITET 500KV BALARAJA | IBT | #4 | CUT OFF 1 - DIAMETER #6 | 7A6 | 500/150kV | 2000 / 1 | Areva | MiCom P821 | 32687102/10/13 | Numerik |  | 1 | 0.2 | 0.07
5 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0015 - PHT 500kV JAWA 7 #1 | PHT 500kV JAWA 7 #1 | TRS-3413-008.008-B0021 - 7B2 DIAMETER #2 500kV | 7B2 DIAMETER #2 500kV | DIAMETER #2 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV JAWA 7 | #1 | CUT OFF 3 - DIAMETER #2 | 7B2 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307181 | Numerik |  | 1 | 0.2 | 0.07
6 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0014 - PHT 500kV JAWA 7 #2 | PHT 500kV JAWA 7 #2 | TRS-3413-008.008-B0020 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | DIAMETER #1 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV JAWA 7 | #2 | CUT OFF 3 - DIAMETER #1 | 7B1 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307175 | Numerik |  | 1 | 0.2 | 0.07
7 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0004 - PHT 500kV LENGKONG #1 | PHT 500kV LENGKONG #1 | TRS-3413-008.008-B0022 - 7A3 DIAMETER #3 500kV | 7A3 DIAMETER #3 500kV | DIAMETER #3 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV LENGKONG | #1 | CUT OFF 1 - DIAMETER #3 | 7A3 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307179 | Numerik |  | 1 | 0.2 | 0.07
8 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0013 - PHT 500kV LENGKONG #2 | PHT 500kV LENGKONG #2 | TRS-3413-008.008-B0001 - 7A4 DIAMETER #4 500kV | 7A4 DIAMETER #4 500kV | DIAMETER #4 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV LENGKONG | #2 | CUT OFF 1 - DIAMETER #4 | 7A4 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307174 | Numerik |  | 1 | 0.2 | 0.07
9 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0005 - PHT 500kV SURALAYA #1 | PHT 500kV SURALAYA #1 | TRS-3413-008.008-B0016 - 7B3 DIAMETER #3 500kV | 7B3 DIAMETER #3 500kV | DIAMETER #3 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV SURALAYA | #1 | CUT OFF 3 - DIAMETER #3 | 7B3 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307178 | Numerik |  | 1 | 0.2 | 0.07
10 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0012 - PHT 500kV SURALAYA #2 | PHT 500kV SURALAYA #2 | TRS-3413-008.008-B0003 - 7B4 DIAMETER #4 500kV | 7B4 DIAMETER #4 500kV | DIAMETER #4 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV SURALAYA | #2 | CUT OFF 3 - DIAMETER #4 | 7B4 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307180 | Numerik |  | 1 | 0.2 | 0.07
11 | TRS-3413-008.008 - GITET 500kV BALARAJA | #N/A | PHT 500kV KEMBANGAN (FUTURE) #1 | TRS-3413-008.008-B0025 - 7B5 DIAMETER #5 500kV | 7B5 DIAMETER #5 500kV | DIAMETER #5 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV KEMBANGAN (FUTURE) | #1 | CUT OFF 3 - DIAMETER #5 | 7B5 | 500kV
12 | TRS-3413-008.008 - GITET 500kV BALARAJA | #N/A | PHT 500kV KEMBANGAN (FUTURE) #2 | TRS-3413-008.008-B0028 - 7B6 DIAMETER #6 500kV | 7B6 DIAMETER #6 500kV | DIAMETER #6 | ULTG CIKUPA | GITET 500KV BALARAJA | PHT 500kV KEMBANGAN (FUTURE) | #2 | CUT OFF 3 - DIAMETER #6 | 7B6 | 500kV
13 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0007 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | TRS-3413-008.008-B0007 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | DIAMETER #1 | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #1 | 7AB1 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307173 | Numerik |  | 1 | 0.2 | 0.07
14 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0017 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | TRS-3413-008.008-B0017 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | DIAMETER #2 | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #2 | 7AB2 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307171 | Numerik |  | 1 | 0.2 | 0.07
15 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0019 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | TRS-3413-008.008-B0019 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | DIAMETER #3 | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #3 | 7AB3 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307176 | Numerik |  | 1 | 0.2 | 0.07
16 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0009 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | TRS-3413-008.008-B0009 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | DIAMETER #4 | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #4 | 7AB4 | 500kV | 2000 / 1 | Areva | MiCom P821 | 3307177 | Numerik |  | 1 | 0.2 | 0.07
17 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0024 - 7AB5 DIAMETER #5 500kV | 7AB5 DIAMETER #5 500kV | TRS-3413-008.008-B0024 - 7AB5 DIAMETER #5 500kV | 7AB5 DIAMETER #5 500kV | DIAMETER #5 | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #5 | 7AB5 | 500kV | 2000 / 1 | Siemens | 7VK61 | BF1201064277 | Numerik |  | 1 | 0.2 | 0.07
18 | TRS-3413-008.008 - GITET 500kV BALARAJA | TRS-3413-008.008-B0027 - 7AB6 DIAMETER #6 500kV | 7AB6 DIAMETER #6 500kV | TRS-3413-008.008-B0027 - 7AB6 DIAMETER #6 500kV | 7AB6 DIAMETER #6 500kV | DIAMETER #6 | ULTG CIKUPA | GITET 500KV BALARAJA |  |  | CUT OFF 2 - DIAMETER #6 | 7AB6 | 500kV | 2000 / 1 | Areva | MiCom P821 | 32687103/10/13 | Numerik |  | 1 | 0.2 | 0.07
19 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0001 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-194.194-B0009 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | DIAMETER #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT | #1 | CUT OFF 3 - DIAMETER #1 | 7B1 | 500/150kV
20 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0004 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | TRS-3413-194.194-B0010 - 7B2 DIAMETER #2 500kV | 7B2 DIAMETER #2 500kV | DIAMETER #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT | #2 | CUT OFF 3 - DIAMETER #2 | 7B2 | 500/150kV
21 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0082 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | TRS-3413-194.194-B0008 - 7A4 DIAMETER #4 500kV | 7A4 DIAMETER #4 500kV | DIAMETER #4 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV GANDUL | #1 | CUT OFF 1 - DIAMETER #4 | 7A4 | 500kV
22 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-DUM.000-B0075 - PHT 500kV KEMBANGAN #2 | PHT 500kV KEMBANGAN #2 | TRS-3413-194.194-B0007 - 7A3 DIAMETER #3 500kV | 7A3 DIAMETER #3 500kV | DIAMETER #3 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV KEMBANGAN | #2 | CUT OFF 1 - DIAMETER #3 | 7A3 | 500kV
23 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | IBT (FUTURE) #3 500/150kV (HV) | #N/A | 7B3 DIAMETER #3 500/150kV | DIAMETER #3 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT (FUTURE) | #3 | CUT OFF 3 - DIAMETER #3 | 7B3 | 500/150kV
24 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | IBT (FUTURE) #4 500/150kV (HV) | #N/A | 7B4 DIAMETER #4 500/150kV | DIAMETER #4 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | IBT (FUTURE) | #4 | CUT OFF 3 - DIAMETER #4 | 7B4 | 500/150kV
25 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | PHT 500kV MUARAKARANG (FUTURE) #1 | TRS-3413-194.194-B0006 - 7A2 DIAMETER #2 500kV | 7A2 DIAMETER #2 500kV | DIAMETER #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG (FUTURE) | #1 | CUT OFF 1 - DIAMETER #2 | 7A2 | 500kV
26 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | #N/A | PHT 500kV MUARAKARANG (FUTURE) #2 | TRS-3413-194.194-B0005 - 7A1 DIAMETER #1 500kV | 7A1 DIAMETER #1 500kV | DIAMETER #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI | PHT 500kV MUARAKARANG (FUTURE) | #2 | CUT OFF 1 - DIAMETER #1 | 7A1 | 500kV
27 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0013 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | TRS-3413-194.194-B0013 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | DIAMETER #1 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #1 | 7AB1 | 500kV
28 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0014 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | TRS-3413-194.194-B0014 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | DIAMETER #2 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #2 | 7AB2 | 500kV
29 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0015 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | TRS-3413-194.194-B0015 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | DIAMETER #3 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #3 | 7AB3 | 500kV
30 | TRS-3413-194.194 - GISTET 500kV DURIKOSAMBI | TRS-3413-194.194-B0016 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | TRS-3413-194.194-B0016 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | DIAMETER #4 | ULTG DURIKOSAMBI | GISTET 500KV DURIKOSAMBI |  |  | CUT OFF 2 - DIAMETER #4 | 7AB4 | 500kV
31 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0006 - IBT #1 500/150kV (HV) | IBT #1 500/150kV (HV) | TRS-3413-004.004-B0010 - 7A1 DIAMETER #1 500kV | 7A1 DIAMETER #1 500kV | DIAMETER #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #1 | CUT OFF 1 - DIAMETER #1 | 7A1 | 500/150kV
32 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0005 - IBT #2 500/150kV (HV) | IBT #2 500/150kV (HV) | TRS-3413-004.004-B0003 - 7A2 DIAMETER #2 500kV | 7A2 DIAMETER #2 500kV | DIAMETER #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | IBT | #2 | CUT OFF 1 - DIAMETER #2 | 7A2 | 500/150kV
33 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-DUM.000-B0072 - PHT 500kV DURIKOSAMBI #1 | PHT 500kV DURIKOSAMBI #1 | TRS-3413-DUM.000-B0054 - 7B3 DIAMETER #3 500kV | 7B3 DIAMETER #3 500kV | DIAMETER #3 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #1 | CUT OFF 3 - DIAMETER #3 | 7B3 | 500kV
34 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0018 - PHT 500kV DURIKOSAMBI #2 | PHT 500kV DURIKOSAMBI #2 | TRS-3413-004.004-B0017 - 7B4 DIAMETER #4 500kV | 7B4 DIAMETER #4 500kV | DIAMETER #4 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV DURIKOSAMBI | #2 | CUT OFF 3 - DIAMETER #4 | 7B4 | 500kV
35 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0007 - PHT 500kV GANDUL #1 | PHT 500kV GANDUL #1 | TRS-3413-004.004-B0002 - 7B1 DIAMETER #1 500kV | 7B1 DIAMETER #1 500kV | DIAMETER #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #1 | CUT OFF 3 - DIAMETER #1 | 7B1 | 500kV
36 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0008 - PHT 500kV GANDUL #2 | PHT 500kV GANDUL #2 | TRS-3413-004.004-B0011 - 7B2 DIAMETER #2 500kV | 7B2 DIAMETER #2 500kV | DIAMETER #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | PHT 500kV GANDUL | #2 | CUT OFF 3 - DIAMETER #2 | 7B2 | 500kV
37 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | BALARAJA (FUTURE) #1 | TRS-3413-004.004-B0015 - 7A4 DIAMETER #4 500kV | 7A4 DIAMETER #4 500kV | DIAMETER #4 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | BALARAJA (FUTURE) | #1 | CUT OFF 1 - DIAMETER #4 | 7A4 | 500kV
38 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | #N/A | BALARAJA (FUTURE) #2 | TRS-3413-004.004-B0013 - 7A3 DIAMETER #3 500kV | 7A3 DIAMETER #3 500kV | DIAMETER #3 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN | BALARAJA (FUTURE) | #2 | CUT OFF 1 - DIAMETER #3 | 7A3 | 500kV
39 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0001 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | TRS-3413-004.004-B0001 - 7AB1 DIAMETER #1 500kV | 7AB1 DIAMETER #1 500kV | DIAMETER #1 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #1 | 7AB1 | 500kV
40 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0004 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | TRS-3413-004.004-B0004 - 7AB2 DIAMETER #2 500kV | 7AB2 DIAMETER #2 500kV | DIAMETER #2 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #2 | 7AB2 | 500kV
41 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0014 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | TRS-3413-004.004-B0014 - 7AB3 DIAMETER #3 500kV | 7AB3 DIAMETER #3 500kV | DIAMETER #3 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #3 | 7AB3 | 500kV
42 | TRS-3413-004.004 - GISTET 500kV KEMBANGAN | TRS-3413-004.004-B0016 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | TRS-3413-004.004-B0016 - 7AB4 DIAMETER #4 500kV | 7AB4 DIAMETER #4 500kV | DIAMETER #4 | ULTG DURIKOSAMBI | GISTET 500KV KEMBANGAN |  |  | CUT OFF 2 - DIAMETER #4 | 7AB4 | 500kV

## CBF&CCP (hidden)
APP DURIKOSAMBI
NO | GI / GIS | BAY | RATIO (kV) | RATIO CT | CBF & CCP
[5 empty] | MERK/TYPE | NO SERI | SETTING |  |  | KETERANGAN
1 | GITET Balaraja | Cut-Off 1 Diameter 1 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307182 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025276/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025277/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 2 Diameter 1 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307173 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  | Cut-Off 3 Diameter 1 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307175 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.15
[7 empty] | t2 | : | 0.3
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025312/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025321/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 1 Diameter 2 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307172 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025273/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025318/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 2 Diameter 2 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307171 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  | Cut-Off 3 Diameter 2 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307181 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025274/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025278/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 1 Diameter 3 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307179 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025315/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025275/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 2 Diameter 3 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307176 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  | Cut-Off 3 Diameter 3 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307178 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025279/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025317/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 1 Diameter 4 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307174 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025316/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | Areva / MCAG 34 | 10025313/08/07 | Is | : | 0.2 A | CCP 2
|  | Cut-Off 2 Diameter 4 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307177 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  | Cut-Off 3 Diameter 4 | 500000/100 | 2000-01-01 | Areva / MiCom P821 | 3307180 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP
[7 empty] | t | : | 0.07
|  |  |  | 2000-01-01 | AREVA / MCAG 34 | 10025311/08/07 | Is | : | 0.2 A | CCP 1
|  |  |  | 2000-01-01 | AREVA / MCAG 34 | 10025320/08/07 | Is | : | 0.2 A | CCP 2
|  | Diameter 5 | 500000/100 | 1000/1 | Siemens / Siprotec 7VK61 | BF1201064272 | Is | : | 0.2 A | CBF 7A5
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP 7A5
[7 empty] | t | : | 0.07
|  |  |  | 1000/1 | Siemens / SIPROTEC 7UT61 | BF1201067964 | Id 1 | : | 0.2 PU | CCP 1 F871
[7 empty] | Id 2 | : | 8 PU
|  |  |  | 2000-01-01 | Siemens / SIPROTEC 7UT61 | BF1201067961 | Id 1 | : | 0.2 PU | CCP 1 F872
[7 empty] | Id 2 | : | 8 PU
|  |  |  | 2000-01-01 | Siemens / SIPROTEC 7VK61 | BF1201064277 | Is | : | 0.2 A | CBF 7AB5
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP 7AB5
[7 empty] | t | : | 0.07
|  | Diameter 6 | 500000/100 | 2000/1 | Alstom / MiCom P841 | 32687102/10/13 | Is | : | 0.2 A | CBF 7A6
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP 7A6
[7 empty] | t | : | 0.07
|  |  |  | 2000/1 | Alstom / MiCom P643 | 32677515/09/13 | Id 1 | : | 0.2 PU | CCP 1 F871
[7 empty] | Id 2 | : | 8 PU
|  |  |  | 2000-01-01 | Alstom / MiCom P643 | 32677514/09/13 | Id 1 | : | 0.2 PU | CCP 1 F872
[7 empty] | Id 2 | : | 8 PU
|  |  |  | 2000-01-01 | Alstom / MiCom P841 | 32687103/10/13 | Is | : | 0.2 A | CBF 7AB6
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
[7 empty] | Is | : | 0.2 A | SZP 7AB6
[7 empty] | t | : | 0.07
2 | GIS Alam Sutera |  |  | 300/1 | Alstom / MiCom P141 | 32184423/06/12 | Is |  | 0.2 | CBF
[7 empty] | t1 |  | 0.1
0.25
32184422/06/12
32184424/06/12
32184420/06/12
32184425/06/12
32184427/06/12
32184421/06/12
32184426/06/12
3 | GIS Lontar | PMT 5A1 | 150000/100 | 474817 | NR / RCS-921 | 7430100900901 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7431100900201 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5AB1 | 150000/100 | 474817 | NR / RCS-921 | 7430100900801 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  | PMT 5B1 | 150000/100 | 474817 | NR / RCS-921 | 7430100900401 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7786100900201 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5A2 | 150000/100 | 474817 | NR / RCS-921 | 7430100900901 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7431100900101 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5AB2 | 150000/100 | 474817 | NR / RCS-921 | 7430100900301 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  | PMT 5B2 | 150000/100 | 474817 | NR / RCS-921 | 7430100901001 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7786100900101 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5A3 | 150000/100 | 474817 | NR / RCS-921 | 7430100900501 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7431100900301 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5AB3 | 150000/100 | 474817 | NR / RCS-921 | 7430100901201 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  | PMT 5B3 | 150000/100 | 474817 | NR / RCS-921 | 7430100900101 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7786100900401 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5A4 | 150000/100 | 474817 | NR / RCS-921 | 7430100900601 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7431100900401 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0
|  | PMT 5AB4 | 150000/100 | 474817 | NR / RCS-921 | 7430100900201 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  | PMT 5B4 | 150000/100 | 474817 | NR / RCS-921 | 7430100900701 | Is | : | 0.2 A | CBF
[7 empty] | t1 | : | 0.1
[7 empty] | t2 | : | 0.25
|  |  | 150000/100 | 474817 | NR / RCS-922 | 7786100900301 | Is | : | 0.3 A | STUB
[7 empty] | t | : | 0